# SECTION 01354 (SECTION 01 35 46)

## CONSTRUCTION INDOOR AIR QUALITY MANAGEMENT

- GENERAL

  - SECTION INCLUDES

    - Special requirements for Indoor Air Quality (IAQ) management during construction operations.

      - Control of emissions during construction.

      - Moisture control during construction.

    - Procedures for testing baseline IAQ.  Baseline lAQ requirements specify maximum indoor pollutant concentrations for acceptance of the facility.

    - RELATED SECTIONS

    - Section 01810-Commissioning.

    - Section 02070-Minor Demolition for Remolding.

    - Section 02222-Building Demolition.

    - DEFINITIONS

    - Definitions pertaining to sustainable development:  As defined in ASTM E2114.

    - Adequate ventilation: Ventilation, including air circulation and air changes, required to cure materials, dissipate humidity, and prevent accumulation of particulates, dust, fumes, vapors, or gases.

    - Hazardous Materials:  Any material that is regulated as a hazardous material in accordance with 49 CFR 173, requires a Material Safety Data Sheet (MSDS) in accordance with 29 CFR 1910.1200, or which during end use, treatment, handling, storage, transportation or disposal meets or has components which meet or have the potential to meet the definition of a Hazardous Waste in accordance with 40 CFR 261. Throughout this specification, hazardous material includes hazardous chemicals.

      - Hazardous materials include: Pesticides, biocides, and carcinogens as listed by recognized authorities, such as the Environmental Protection Agency (EPA) and the International Agency for Research on Cancer (IARC).

    - Indoor Air Quality (IAQ):  The composition and characteristics of the air in an enclosed space that affect the occupants of that space.  The indoor air quality of a space refers to the relative quality of air in a building with respect to contaminants and hazards and is determined by the level of indoor air pollution and other characteristics of the air, including those that impact thermal comfort such as air temperature, relative humidity and air speed.

    - Interior Final Finishes:  Materials and products that will be exposed at interior occupied spaces including flooring, wall covering, finish carpentry, and ceilings.

    - Packaged Dry Products:  Materials and products that are installed in dry form and are delivered to the site in manufacturer's packaging; including carpets, resilient flooring, ceiling tiles, and insulation.

    - Wet Products:  Materials and products installed in wet form, including paints, sealants, adhesives, special coatings, and other materials which require curing.

  - QUALITY ASSURANCE

    - Inspections and Testing Lab Qualifications:  Minimum of 5 years experience in performing the types of testing specified herein.

    - Coordinate with Section 01740-Cleaning.

    - PRECONSTRUCTION MEETING

    - Shall not occur without Indoor Air Quality Plan accepted by the Project Consultant and the Owner.  After award of Contract and prior to the commencement of the Work, schedule and conduct meeting with Owner and Project Consultant to discuss the proposed IAQ Management Plan and to develop mutual understanding relative to details of environmental protection.

    - SUBMITTALS

- ************************************************************************************************************************NOTE TO SPECIFIER:  Make selection below to suit Project.

- ***********************************************************************************************************************

    - Indoor Air Quality (IAQ) Plan:  Submit [3] <Insert number> copies of plan not less than 10 days before the Waste Management Pre-construction meeting, prepare and submit an IAQ Management Plan including, but not limited to, the following:

      - Procedures for control of emissions during construction.

        - Identify schedule for application of interior finishes.

      - Procedures for moisture control during construction.

        - Identify porous materials and absorptive materials.

        - Identify schedule for inspection of stored and installed absorptive materials.

      - Revise and resubmit Plan as required by Owner.

        - Acceptance of Contractor’s Plan will not relieve the Contractor of responsibility for compliance with applicable environmental regulations.

      - Indoor Air Quality Plan must be accepted by the Project Consultant and Owner.  Acceptance by Project Consultant and Owner does not relieve the Contractor of responsibility of compliance with applicable environmental regulations.

    - Product Data:

      - Submit product data for filtration media used during construction and during operation.  Include Minimum Efficiency Reporting Value (MERV).

      - Material Safety Data Sheets (MSDS):  Submit MSDS for inclusion in Operation and Maintenance Manual for the following products.  Coordinate with Section 01830-Operations and Maintenance.

        - Adhesives.

        - Carpet.

        - Caulking and sealants.

        - Cleaning products.

        - Clear finish for wood surfaces.

        - Fireproofing and firestopping.

        - Floor and wall patching/leveling materials.

        - Insulating materials.

        - Lubricants.

        - Paint.

    - Inspection and Test Reports:

      - Moisture control inspections.

      - Moisture content testing.

      - Moisture penetration testing.

      - Microbial growth testing.

    - Submit documentation for LEED IAQ Management Plan, During Construction, Credit 3.1 compliance.

  - QUALITY ASSURANCE

    - Coordinate with Section 01740-Cleaning.

    - PRODUCTS (NOT USED)

    - EXECUTION

    - IAQ MANAGEMENT - EMISSIONS CONTROL

    - During construction operations, follow the recommendations in SMACNA IAQ Guidelines for Occupied Buildings under Construction.

    - HVAC Protection:

      - Seal return registers during construction operations.

      - Provide temporary exhaust during construction operations

      - To the greatest extent possible, isolate and/or shut down the return side of the HVAC system during construction.  When ventilation system must be operational during construction activities, provide temporary filters.

    - Source Control:  Provide low and zero VOC materials as specified.

      - Smoking is prohibited inside the building and within 25 feet of building entrances once the building is closed.  Provide signage on the site during construction that clearly states this requirement.  Provide and locate designated smoking areas with extinguishing devices, at least 25 feet away from entries, outdoor intakes and operable windows.

    - Pathway Interruption:  Isolate areas of work as necessary to prevent contamination of clean or occupied spaces.  Provide pressure differentials and/or physical barriers to protect clean or occupied spaces.

    - Housekeeping:  During construction, maintain project and building products and systems to prevent contamination of building spaces.

- ***********************************************************************************************************************NOTE TO SPECIFIER:  Make selection below to suit Project.

- ***********************************************************************************************************************

    - Temporary Ventilation:  Provide an ACH (air changes per hour) of [1.5] [xxxx] or more and as follows:

      - Provide minimum 48 hour pre-ventilation of packaged dry products prior to installation.  Remove from packaging and ventilate in a secure, dry, well-ventilated space free from strong contaminant sources and residues.  Provide a temperature range of 60 degrees F minimum to 90 degree F maximum continuously during the ventilation period.  Do not ventilate within limits of Work unless otherwise approved by Project Consultant.

      - Provide adequate ventilation during and after installation of interior wet products and interior final finishes.

- ***********************************************************************************************************************NOTE TO SPECIFIER:  Make selection below to suit Project.

- ***********************************************************************************************************************

      - Provide filtration media with a Minimum Efficiency Reporting Value (MERV) of 8 as determined by ASHRAE 52.2 during construction [and during Owner occupancy].  Coordinate with work of Division-15, Heating Ventilating and Air Conditioning (HVAC).

    - Scheduling:  Schedule construction operations involving wet products prior to packaged dry products to the greatest extent possible.

    - Air Quality Testing:  Refer to Division 15.

    - IAQ MANAGEMENT - MOISTURE CONTROL

    - Housekeeping:

      - Keep materials dry.  Protect stored on-site and installed absorptive materials from moisture damage.

      - Verify that installed materials and products are dry prior to sealing and weatherproofing the building envelope.

      - Install interior absorptive materials only after building envelope is sealed and weatherproofed.

    - Inspections:  Document and report results of inspections; state whether of not inspections indicate satisfactory conditions.

      - Examine materials for dampness as they arrive.  If acceptable to Project Consultant/Owner, dry damp materials completely prior to installation; otherwise, reject materials that arrive damp.

      - Examine materials for mold as they arrive and reject materials that arrive contaminated with mold.

- ***********************************************************************************************************************NOTE TO SPECIFIER:  Make selection below to suit Project.

- ***********************************************************************************************************************

      - Inspect stored and installed absorptive materials regularly for dampness and mold growth.  Inspect [weekly,] [after each rain event,] [xxxx].

        - Where stored on-site or installed absorptive materials become wet, notify [Project Consultant] [Owner].  Inspect for damage.  If acceptable to Project Consultant/Owner, dry completely prior to closing in assemblies; otherwise, remove and replace with new materials.

      - Site drainage:  Verify that final grades of site work and landscaping drain surface water and ground water away from the building.

      - Weather-proofing:  Inspect moisture control materials as they are being installed.  Include the following:

        - Air barrier:  Verify air barrier is installed without punctures and/or other damage.  Verify air barrier is sealed completely.

        - Flashing:  Verify correct shingling of the flashing for roof, walls, windows, doors, and other penetrations.

        - Insulation layer:  Verify insulation is installed without voids.

        - Roofing:  In accordance with ASTM D7186 Standard Practice for Quality Assurance Observation of Roof Construction and Repair

      - Plumbing:  Verify satisfactory pressure test of pipes and drains is performed before closing in and insulating lines.

      - HVAC:  Inspect HVAC system as specified in Section 01810-Commissioning.

    - Schedule:

      - Schedule work such that absorptive materials, including but not limited to porous insulations, paper-faced gypsum board, ceiling tile, and finish flooring, are not installed until they can be protected from rain and construction-related water.

      - Weather-proof as quickly as possible.  Schedule installation of moisture-control materials, including but not limited to air barriers, flashing, exterior sealants and roofing, at the earliest possible time.

    - Testing for Moisture Content:  Test moisture content of porous materials and absorptive materials to ensure that they are dry before sealing them into an assembly.  Document and report results of testing.  Where tests are not satisfactory, dry materials and retest.  If satisfactory results cannot be obtained with retest, remove and replace with new materials.

- ************************************************************************************************************************NOTE TO SPECIFIER:  Make selection below to suit Project.

- ***********************************************************************************************************************

      - Concrete:  [Moisture test prior to finish flooring application as specified in Division 09.] [Moisture test per one or more of the following; unless otherwise indicated, acceptable upper limits for concrete are < 4 percent top inch; < 85 percent headspace RH; <3 lbs/1000ft2/day:

        - ASTM D4263 Test Method for Indicating Moisture in Concrete by the Plastic Sheet Method

        - ASTM F1869 Test Method for Measuring Moisture Vapor Emission Rate of Concrete Subfloor Using Anhydrous Calcium Chloride

        - ASTM F2170 Test Method for Determining Relative Humidity in Concrete Floor Slabs Using In Situ Probes.

      - Wood:  Moisture test per ASTM D4444-Standard Test Methods for Use and Calibration of Hand-Held Moisture Meters; unless otherwise indicated acceptable upper limits for wood products are < 20 percent at center of piece; < 15 percent at surface.

      - Gypsum Board, Gypsum Plaster, Insulation, and other absorptive materials:  Moisture test with a Pinless Moisture Meter to assess patterns of moisture, if any.

    - Testing for Moisture Penetration:

      - Windows:  Test per ASTM E1105 Test Method for Field Determination of Water Penetration of Installed Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform or Cyclic Static Air Pressure Difference; unless otherwise indicated, acceptable upper limits are no leakage for 15 minutes.

      - Horizontal Waterproofing (not roofing):  Test as per ASTM D5957 Standard Guide for Flood Testing Horizontal Waterproofing Installations; acceptable upper limits are no leakage for 15 minutes.

      - Masonry:  Test as per ASTM C1601 Standard Test Method for Field Determination of Water Penetration of Masonry Wall Surfaces; acceptable upper limits are no leakage for 15 minutes.

      - Exterior Walls:

        - Air tightness of the enclosure test:  ASTM E779 Standard Test Method for Determining Air Leakage Rate by Fan Pressurization or ASTM E1827 Standard Test Methods for Determining Air tightness of Buildings Using an Orifice Blower Door.

        - Water Leakage:  Review per ASTM E2128 Standard Guide for Evaluating Water Leakage of Building Walls.

    - Testing for Support of Microbial Growth:  Test and report in accordance with ASTM D6329 Standard Guide for Developing Methodology for Evaluating the Ability of Indoor Materials to Support Microbial Growth Using Static Environmental Chambers.  Indicate susceptibility of product or material to colonization and amplification of microorganisms.  Identify microorganisms and conditions of testing.

      - Normal Conditions:  Perform testing at 35 degrees Centigrade and 50 percent relative humidity.

      - Extreme Conditions:  Perform worst case scenarios screening tests by providing an atmosphere where environmental conditions may be favorable for microbial growth.

      - Perform testing for the following:

        - Fireproofing material on appropriate substrate.

        - Ceiling tile.

        - Wall covering.

END OF SECTION