# SECTION 11426 (23 38 14)

## KITCHEN FILTER TYPE EXHAUST HOOD

GENERAL

SECTION INCLUDES

Kitchen filter type exhaust hood system.

RELATED SECTIONS

Section 15060 - Hangers and Supports.

Section 15810 - Ducts.

REFERENCES

ASTM A120 - Black Steel Pipe and Hot-Dipped Zinc Coated (Galvanized), Welded and Seamless for Ordinary Uses.

ASTM B88 - Specification for Seamless Copper Water Tube.

FAC Chapter 64E-11, FAC-Food Hygiene.

NFPA 70 - National Electric Code.

NFPA 90 - Air Conditioning and Ventilation Systems.

NFPA 96 - Removal of Smoke and Grease Laden Vapors from Commercial Cooking      Equipment.

Underwriters Laboratories (UL) 762.

National Sanitation Foundation (NSF).

SUBMITTALS

Submit manufacturer's installation shop drawings with instructions.

Submit operation and maintenance data.  Include replacement parts lists.

DELIVERY, STORAGE AND HANDLING

Deliver products to site in factory fabricated protective containers with factory installed shipping skids and lifting lugs.

Store in clean dry place and protect from weather and construction traffic.  Handle carefully to avoid damage to components, enclosures and finish.

PRODUCTS

ACCEPTABLE MANUFACTURERS - FILTER TYPE

CaptiveAire Model ND-2-PSP-F

Gaylord Model FX-BDL

Ventmaster Model GL .

KITCHEN HOOD

Hood shall be designed with a minimum of one foot overhang of the cooking equipment and constructed of minimum 18 gauge or heavier Series 300 with a number 4 polished stainless steel exposed surface finish, be capable of extracting a minimum of 65 percent of generated grease through a bank of filters and be manually operated by an ON/OFF push-button switch on the UDS riser (if applicable) to activate the exhaust/supply fans whenever cooking operations occur.  The hood shall be provided with a rooftop exhaust/supply fan assembly by the Mechanical Contractor capable of providing 80 percent supply air makeup with the remaining 20 percent taken from the air conditioned kitchen or adjacent areas in order to maintain a negative pressure in the kitchen.  Recessed florescent lights shall be prewired and controlled by a manual ON/OFF switch.  The grease extraction percentage shall be verified by an independent testing laboratory and notarized prior to submittal.

The hood supply air makeup shall be accomplished by a low velocity (maximum of 150 FPM), perforated, vertical air discharge perimeter supply air plenum along the full front length of the hood.  The perimeter supply plenum shall be installed a maximum of 8’-0” above finished floor or a maximum of 1’-6” above the bottom of the hood whichever is applicable.  The supply air makeup duct shall be provided with a fusible link fire damper.

Manually depress the “RUN” button on the hood control panel to energize the exhaust fan start coils in order to operate the exhaust and supply fans.  Startup by use of programmable microprocessor equipment is PROHIBITED.

Filter:  Constructed of stainless steel and manufactured by the hood manufacturer.

Hood shall be UL listed under the category “Grease Extractors for Exhaust Ducts” and in accordance with all the recommendations of NFPA 96.

FIRE PROTECTION SYSTEM

Hood shall be internally pre-piped for the fire suppression system at the factory by the hood manufacturer.  System shall be a UL listed wet chemical automatic fire suppression system to protect the plenum, exhaust duct, two burner Expando unit, steam kettle and other cooking equipment requiring protection in accordance with code and UL requirements and installed in compliance with the current UL Standard 300.  Provide all electrical appurtenances necessary to properly interconnect the fire protection control panel to the hood control panel in order to activate the fire fan when the system goes into the fire mode.

The fire suppression system shall be a pre-engineered dedicated system with a cartridge-operated type liquid agent such as Ansul R-102 distributed to a network of fixed nozzles within the hood.  The tank containing the wet chemical liquid agent shall be fabricated of stainless steel.  Other approved fire suppression systems are Amerex and Prochem.

The hood and fire suppression system shall be installed by a licensed, factory authorized Contractor in accordance with the manufacturer’s recommendations and in compliance with all codes.  Schematic drawings shall be prepared by a licensed engineer and submitted prior to the commencement of work.

The piping and conduit shall be run concealed from view whenever possible.  All exposed piping and conduit shall be chrome plated or stainless steel.  All drops and nozzles shall be of the “high proximity” type.  All drops and nozzle locations shall be verified and coordinated with the actual final equipment location.

Provide UL listed “Quick Seals” to seal all penetrations through the hood.  All exposed piping to be stainless steel or chrome plated.  Sleeves for pipe penetrations through duct and plenum are not approved.

A point-of-use, UL listed gas solenoid valve interconnected to the fire suppression system shall be provided by the Contractor responsible for the gas line installation.

A remote pull station shall be provided at exit point to the building exterior.

A point-of-use, UL listed gas solenoid valve interconnected to the fire suppression system shall be provided by the Contractor responsible for the gas line installation.

SUPPLY FAN

Supply fan shall be a rooftop UL listed and compatible for use with commercial cooking equipment.  The fan shall be provided with permanent washable filters, belt drive, insulated roof curb, bird screen, quick disconnect thermal overload protection and adjustable pulleys.  The roof curb height shall be 18 inches minimum above the FINISHED roof.

EXHAUST FAN

Exhaust fan shall be a rooftop UL 762 listed and compatible for use with commercial cooking equipment. Fan shall be provided with a grease reservoir, belt drive, insulated roof curb, bird screen, quick disconnect thermal overload protection, adjustable pulleys and adjustable and removable come cover.  Fan shall not exceed 1000 RPM in order to insure quiet operation.  The roof curb height shall be 18 inches minimum above the FINISHED roof.

EXECUTION

INSTALLATION

Kitchen hood shall be installed in an island type fashion unless otherwise shown on the drawings.

Electrical connections made inside the kitchen hood wet chemical fire suppression system control box are prohibited.

FIELD QUALITY CONTROL

Fire Protection System:

Verify that the exhaust ductwork, steam kettle, the two burner Expando unit and other grease generating equipment are protected by the hood fire extinguishing system.

In the event of fire during building occupancy, the exhaust fan shall continue to run for the purpose of smoke evacuation and the supply fan shall be deactivated.  Should the hood be UL listed and approved for an exhaust duct fire damper, the damper shall remain open.  The cooking equipment shunt breakers shall trip and the building fire alarm annunciator shall be activated.

3.3	TEST AND ADJUST

A.	Kitchen exhaust hood startup, testing and adjustment shall be performed by the manufacturer’s factory technician.

Exhaust and supply fan startup, testing and adjustments shall be performed by the manufacturer’s factory technician to insure proper exhaust and supply air operation.

Fire system testing and certification of the fire protection system shall be performed by the fire suppression system installer in the presence of the Owner.

CLEANING

Clean oil, grease, fingerprints and other grime from all equipment.

Remove debris and waste material resulting from the installation.

DEMONSTRATION

Demonstrate the complete operation of the system.

3.5	TRAINING

A.	Provide the service of the manufacturer’s factory technician for one four hour session to instruct the Owner’s maintenance personnel in the operation of the kitchen hood and control systems.

Manufacturer shall provide a seven day advance notice to the Contractor and the Project Consultant of the training day.

Manufacturer shall provide a video tape demonstration and instructions of the system’s startup and operation.

Manufacturer shall submit clearly labeled contents on a standard DVD disk format to the Owner.

3.5	DISPLAY OF SEQUENCE OF OPERATION

A.	Submit for approval after installation and demonstration are complete, a simplified sequence of operation and a utility connection diagram geared to a non-technical individual of high school education explaining the system operation and

corresponding to the actual devices.  Upon approval by the Owner, mount one copy  of the sequence of operation behind a plexiglass or lexan cover applied to the interior cover of the hood control panel hinged cover.

END OF SECTION