# SECTION 13802 (27 53 13)

## CLOCK CONTROL

GENERAL

SECTION INCLUDES

A complete clock and program system, clocks, buzzers, bells and wiring.

All labor, materials, necessary equipment and services to complete the Clock and Program System work, except for items specifically indicated as "NIC ITEMS."

RELATED WORK

Section16120-Wire and Cables.

Section 16132-Conduit, Fittings, and Supports.

Section 16134-Auxiliary Terminal Panels.

Section 16137-Pull and Junction Boxes.

Section 16138-Outlet Boxes.

SUBMITTALS

Submit shop drawings and product data under provisions of Section 01330-Submittal Procedures.

QUALITY ASSURANCE

All equipment:  Of the same manufacturer.

WARRANTY

Provide a written 1 year guarantee, signed by the Contractor, due on the date of final acceptance.

Include the following provisions:

Guarantee all equipment and the installation to be free of faulty workmanship.

Guarantee all components, including solid state devices, to be free of defects for a period of 1 year from the date of final acceptance.

PRODUCTS

MANUFACTURERS

Acceptable Manufacturers:  Subject to compliance with the specified requirements, provide products by one of the following manufacturers.

(Basis of Design) Dukane Corporation.

National Time.

Cincinnati.

MASTER TIME and PROGRAM CLOCK

Provide the following features for the Master Time and Program Clock:

Micro-processor based unit suitable for flush/semi-flush mounting unless otherwise indicated.  Capable of controlling and correcting an unlimited number of synchronous motor driven clocks.

Subject to compliance with the specified requirements, provide products by one of the following manufacturers.

Cincinnati.

Dukane.

National.

Standard.

Easily programmable by the user through the use of a built-in push button key pad (for a minimum of 100 time events).

Provide 3 program controls to manually activate any one or all simultaneously.

Provide a battery backup system to continue in operation in the event the normal source of power is lost.  Provide the capabilities to protect program memories, maintain proper time, correct and function with the standby power for minimum of 48 hours. Include charger with battery backup system.

The unit:  U. L. approved.

The Master Time and Program Clock:  Subject to meeting the full intent of the specifications provide products by one of the following:

(Basis of Design) Dukane Model Number 24A700.

Rauland.

Standard.

Master Clock time display: indicates AM/PM status.  Military time display will not be acceptable.

Accomplish daylight savings time adjust by nothing more than the flip of a switch.

SECONDARY CLOCKS & BUZZERS:

Manufacturer:  Dukane #24030-10E.

Single dial, 120 volts, synchronous with sweep second hand, white face, black numerals, standard finish, 9 inches or 10 inches round, and flush mounted.

All clocks: as shown on drawings.

Secondary clocks having lexan or other "plastic" type shafts, bearings, or bushings will not be accepted.

Provide 12 inch clocks for gym, auditorium, and dining area.

Provide shatterproof convex crystal and wire guard for all clocks in gym, shops, and locker rooms.

SIGNALING DEVICES

120 Volt 4 inch or 6 inch bells in corridors and as shown on drawings.

120 Volt 10 inch weatherproof bell with guard for outdoors as shown on drawings.

120 Volt buzzer mounted in all clock enclosures.

WIRE

Stranded, copper

#14 THWN/THNN 600 Volts for clocks.

#12 THWN/THNN 600 Volts for bells and buzzers.

Color code the wiring consistently throughout, as per SBBC Standard Color Code

CLOCK/SPEAKER ENCLOSURES

Provide combination clock/speaker enclosures for all rooms, unless otherwise shown on drawings.  Other clock boxes are provided under this section.

EXECUTION

INSTALLATION

Install all equipment under provisions of manufacturer's recommendations.

Connect the program sequence to the zones or services as indicated on the drawings.

All equipment: of the same manufacturer.

Terminate all wiring on terminal block strips in junction boxes, terminal cabinets.  Tag and identify clock and program bell systems.  Install terminal box near master clock as shown on drawings. Do not splice wires for circuiting inside master clock.

Terminal boards: General Electric, Type CR151, Type A2.

Clock system:  Checked out and put into operation by trained factory technician.

The master clock and signaling circuits:  Wired to an emergency circuit, when generator power is available on site.

Provide wiring in conduit.

END OF SECTION