# SECTION 14430 (14 42 17)

## SHAFTWAY VERTICAL WHEELCHAIR LIFTS

GENERAL

SECTION INCLUDES

Vertical platform wheelchair lift installed within a shaftway.  Note:  The shaftway is built by others.

RELATED SECTIONS

Section 03300-Cast-In-Place Concrete.

Section 04200-Unit Masonry.

Section 09250-Gypsum Board.

Section 13801-Fire Alarm System.

Division 16-Electrical.

REFERENCES

ASME A17.1-Safety Code for Elevators and Escalators.

ASME A17.5-Elevator and Escalator Electrical Equipment.

ASME A18.1-Safety Standard for Platform Lifts and Stairway Chairlifts.

NFPA 70-National Electric Code.

SUBMITTALS

Product Data:  Submit manufacturer's specifications, installation instructions, and general recommendations, including data which substantiates that materials comply with specified requirements.

Certification:  Submit manufacturer's certification that chair lift complies with Florida requirements for accessibility.

Shop Drawings:  Submit shop drawings, including plans, elevations and detail sections of chair lift, mounting hardware, electrical connections, controls, and accessories.  Show anchors, hardware, sills, and other operating equipment required for installation as well as other components not included in manufacturer's standard product data.

Manufacturer's Operating and Maintenance Instructions:  Submit as a closeout submittal under provisions of Section 01780-Closeout Submittals.

Maintenance Demonstration:  Submit DVD video of manufacturer's maintenance demonstration as a closeout submittal under provisions of Section 01780-Closeout submittals.

QUALITY ASSURANCE

Manufacturer Qualifications:  Firm with minimum 10 years documented experience in manufacturing of inclined wheelchair platform lifts of installations of type specified.

Installer Qualifications:  Company approved and trained by specified chair lift manufacturer specializing in installing incline chair lifts with minimum 3 years documented experience.

REGULATORY REQUIREMENTS

Provide platform lifts in compliance with:

ASME A18.1-Safety Standard for Platform Lifts and Stairway Chairlifts.

ASME A17.5-Elevator and Escalator Electrical Equipment.

NFPA 70-National Electric Code.

DELIVERY, STORAGE, and HANDLING

Store products in manufacturer's unopened packaging until ready for installation.

Store components off the ground in a dry covered area, protected from adverse weather conditions.

PROJECT CONDITIONS

Do not use wheelchair lifts for hoisting materials or personnel during construction period.

WARRANTY

Provide manufacturer's warranty for materials and workmanship for a 5 year period.

MAINTENANCE

Provide factory preventative maintenance agreement with 2 annual maintenance inspections for the duration of the 5 year warranty period at no additional cost to the Owner.

PRODUCTS

ACCEPTABLE MANUFACTURERS

Acceptable Manufacturers:  Subject to compliance with the specified requirements, provide lift system(s) by the following manufacturers:

National Wheel-O-Vator Co., Inc.

(Basis of Design) Garaventa Accessibilty.

ThyssenKrupp Access, A ThyssenKrupp Company.

Substitutions:

Will be considered by the Project Consultant and Owner when submitted per requirements of Division-0, Division-1, and Section 01630-Product Substitution Procedures.

UNENCLOSED VERTICAL WHEELCHAIR LIFT

Garaventa Model Genesis Vertical Lift-Shaftway (GVL-SW), with 2 stops, maximum 168 inches floor to floor.

Capacity:  750 lbs rated capacity.

***************************************************************************************************************

NOTE TO SPECIFIER:  Make selection from the following and delete items not selected.

***************************************************************************************************************

Mast Height:

Model GVL-SW -42; 1143 mm (45 inches) maximum lifting height.

Model GVL-SW -60; (63 inches) maximum lifting height.

Model GVL-SW -72; (75 inches) maximum lifting height.

Model GVL-SW -96; (99 inches) maximum lifting height.

Model GVL-SW -120; (123 inches) maximum lifting height.

Model GVL- SW -144; (147 inches) maximum lifting height.

Model GVL- SW -168; (171 inches) maximum lifting height, using hydraulic drive, only.

***************************************************************************************************************

NOTE TO SPECIFIER:  Make selection from the following and delete items not selected.

***************************************************************************************************************

Platform Size and Clear Platform Dimensions:

Compact:  36 inches x 49.5 inches.

Standard:  38 inches x 54 inches.

Mid-Size:  38 inches x 60 inches.

Large:  43 inches x 60 inches.

***************************************************************************************************************

NOTE TO SPECIFIER:  Make selection from the following and delete items not selected.

***************************************************************************************************************

Platform Configuration:

Straight Through Entry/Exit:  Front and rear openings.

90 Degree Entry/Exit:  Front and side openings.

On/Off  Same Side Entry/Exit.

Landing Openings:  Gates shall be self closing type.

Lower Landing:  Door.

Upper Landing:  Door

Upper Landing:  Gate.

***************************************************************************************************************

NOTE TO SPECIFIER:  Make selection from the following and delete items not selected.

***************************************************************************************************************

Door Construction:

Fire Rated Doors:  1-1/2 hour B label rating.  Pre-hung, constructed of 16 gage steel, with a vision panel, delayed action door closer, pull handle and integrated interlock.  Doors mount flush to the inside wall of the shaftway.

Non-Rated Doors:  Pre-hung, on an anodized aluminum frame, with a door closer, pull handle, integrated interlock and constructed with a 16 gage galvanized steel kick plate and upper panel as follows:

***************************************************************************************************************

NOTE TO SPECIFIER:  For non-fire rated doors make selection from the following and delete items not selected.

***************************************************************************************************************

Panels of 16 gage galvanized steel.

Panels of clear Plexiglas.

Panels of bronze Plexiglas.

***************************************************************************************************************

NOTE TO SPECIFIER:  For non-fire rated doors make selection from the following and delete items not selected.

***************************************************************************************************************

Standard molded handle

12 inch offset D-handle

Door Width:

***************************************************************************************************************

NOTE TO SPECIFIER:  Make selection from the following and delete items not selected.

***************************************************************************************************************

Lower Landing:

          - 36 inches wide.

          - 42 inches wide.

Upper landing:

          - 36 inches wide.

          - 42 inches wide.

***************************************************************************************************************

NOTE TO SPECIFIER:  Select the paragraph below if the upper landing will be fitted with a gate instead of a door.  Select only if the shaftway is open at the upper landing and is not fire rated.  Delete if not selected.

***************************************************************************************************************

Upper Gate Construction

42 inches high, pre-hung on an anodized aluminum frame, fitted with a door closer, pull handle, integrated interlock and constructed with a 16 gage galvanized steel kick plate and upper panel as follows:

***************************************************************************************************************

NOTE TO SPECIFIER:  Select one of the following paragraphs for upper gates.  Delete the ones not selected.

***************************************************************************************************************

Panels of 16 gage galvanized steel.

Panels of clear Plexiglas.

Panels of bronze Plexiglas.

***************************************************************************************************************

NOTE TO SPECIFIER:  Edit the following paragraph as required for power operators for doors and gates.  Note that power door operators are required in many jurisdictions.  May be required if ramp is used for entry at lower landing and for certain platform configurations.

***************************************************************************************************************

Power Door Operator: Automatically opens the door/gate when platform arrives at a landing. Will also open at landing by pressing call button or gently pulling the door.

ADA Compliant and obstruction sensitive.

Low voltage, 24 VDC with all wiring concealed.

Provide power operators at the following locations:

***************************************************************************************************************

NOTE TO SPECIFIER:  Select the paragraphs for doors and gates to be equipped with power door operators.  Delete the ones not required.

***************************************************************************************************************

Lower Landing: Door.

Upper landing: Door or Gate.

Lift Components:

Machine Tower:  Custom aluminum extrusion.

Base Frame:  Structural steel tubing.

Platform Side Wall Panels:  16 gage galvanized steel sheet.

Base Mounting and Access to Lift at Lower Landing:

***************************************************************************************************************

NOTE TO SPECIFIER:  At lower landing lift may be mounted in pit to match selected platform size or fitted with a fixed ramp if floor mounted (no pit).  Select one of the two following paragraphs and delete paragraph not used.

***************************************************************************************************************

Floor Mount:  Base of lift shall be mounted on the floor surface of the lower landing.  For access onto the platform provide a ramp of 16 gage galvanized steel sheet with a slip resistant surface.

Pit Mount: Lift to be mounted in pit with dimensions to meet manufacturer’s requirements for the platform size specified.  Pit construction shall be in accordance to Section 03300.

***************************************************************************************************************

NOTE TO SPECIFIER:  Select the flowing paragraph if local jurisdiction requires the void spaces on either side of the mast be covered on the front and top surfaces.  Consult the Genesis Design and Planning Guide for more details.  Delete if not required.

***************************************************************************************************************

Drive Mast Side Wall Panels:  Provide 16 gage galvanized panels and mounting hardware to cover the void between both sides of the mast and the side of the shaftway.  Panels to cover the front and top of the void area to the height of the top surface of the drive mast.

***************************************************************************************************************

NOTE TO SPECIFIER:  Select one of the two following drive paragraphs for Leadscrew Drive or Hydraulic drive type.  Use hydraulic drive when travel distance exceeds 147 inches or when delivery of installation constraints require the mast in two sections.  Delete the drive not selected.

***************************************************************************************************************

Hydraulic Drive:

Drive Type:  Chain hydraulic.

Emergency Operation:  Manual device to lower platform and auxiliary battery power to raise or lower platform.

Safety Devices:

Slack chain safety device.

Shoring device.

Travel Speed:  17fpm.

Motor:  3 HP (2.2 kW); 24 volts DC.

Power Supply:

120 VAC single phase; 60 Hz on a dedicated 15 amp circuit.

***************************************************************************************************************

NOTE TO SPECIFIER:  Select one of the two following paragraphs.  The first is standard and is for heavy, continuous use installations.  Lift is connected directly to building power and batteries are used only for auxiliary emergency power.

***************************************************************************************************************

Powered by continuous mains converted to 24 VDC. equiped with auxiliary power system capable of running lift up and down for a minimum of 5 trips with rated load. *Required for high usage lifts.

Powered by continuously charged battery system.

Platform Controls:  24 VDC control circuit with the following features.

***************************************************************************************************************

NOTE TO SPECIFIER:  Select one of the following two paragraphs for platform direction control.  Standard platform control is a constant pressure rocker switch.  Optional controls consist of illuminated push buttons and courtesy lights.  Delete the one not selected.

***************************************************************************************************************

Direction Control:  Constant pressure rocker switch.

Direction Control:  Illuminated and tactile constant pressure buttons with dual platform courtesy lights and safety light.

Illuminated and audible emergency stop switch shuts off power to lift and activates audio alarm equipped with battery backup.

***************************************************************************************************************

NOTE TO SPECIFIER:  Select one of the two following paragraphs for key operation. Keyless operation is standard. Keyed operation is optional.  Delete the one not selected.

***************************************************************************************************************

Keyless operation.

Keyed operation.

***************************************************************************************************************

NOTE TO SPECIFIER:  Include the following paragraph if required, Emergency phone may be required by the local jurisdiction. Delete if not selected.

***************************************************************************************************************

Emergency Telephone: Lift shall be equipped with Autodialer telephone (ADA compliant)with a stainless steel faceplate.  Telephone shall operate in the event of power failure.  A telephone line shall be supplied to the lift site as specified under Division 16.

Arrival Gong and Digital Floor Display.

Call Station Controls:  24 VDC control circuit with the following features.

Direction Control:  Constant pressure switches.

Directional Control:  Illuminated and tactile constant pressure buttons with illuminated “In Use” indicator.

***************************************************************************************************************

NOTE TO SPECIFIER:  Select one of the two following paragraphs for key operation. Keyless operation is standard. Keyed operation is optional. Delete the one not required.

***************************************************************************************************************

Keyless operation.

Keyed operation.

Call Station Mounting:

***************************************************************************************************************

NOTE TO SPECIFIER:  Select mounting required and delete those not required. Frame mounted call stations are standard for fire rated doors. Frame mounting should not be used at landing with ramp or where a power door operator is used.

***************************************************************************************************************

Lower:

          - Frame mounted.

          - Wall mounted surface.

          - Wall mounted recessed.

Upper:

          - Frame mounted.

          - Wall mounted surface.

          - Wall mounted recessed.

Safety Devices and Features:

Grounded electrical system with upper, lower, and final limit switches.

At all landings a solenoid activated interlock shall electrically monitor that the door is in the closed position and the lock is engaged before lift can move from landing.

Pit stop switch mounted on mast wall.

Electrical disconnect shall shut off power to the lift.

Lifts shall have solid material shielding devices to protect users from machinery or other hazards (including all sides of the area beneath the platform).

Per ASME A18.1:

Must have a solid shaftway (a.k.a: runway) extending from the bottom landing to a height of 42 inches above the top landing.

Must have a minimum of a 42 inch high self closing nonperforated gate at the upper landing.

The underside of the platform must be guarded on all sides by either stationary or telescoping panels.

Finishes

Aluminum Extrusions:  Champagne anodized finish.

Ferrous Components:  Electrostatically applied baked powder finish, fine textured.

Color:  Satin Grey, RAL 7030.

Lift Finish:  Baked powder finish any color from RAL color chart.

EXECUTION

EXAMINATION

Inspect existing conditions, access routes, and installation location.

Notify Project Consultant of any discrepancies or variations between existing conditions and required Work.

Verify that electrical work to be provided by Owner is in place and ready for connection of chair lift.

PREPARATION

Inspect existing stairs, stage wall, access routes, and Owner provided electrical service:

Provide additional bracing/supports under stairs to provide adequate structural support for tube posts and anchors.

INSTALLATION

General:  Install chair lift and accessories under provisions of manufacturer's printed instructions and recommendations and to comply with governing regulations.

Comply with the "American Safety Code for Elevators" A17.1.

Make all electrical connections in compliance with the National Electric Code.

Provide level and plumb installation with proper operation of incline chair lift, standard components, and all specified accessories.

Provide safe and secure work area under provisions of Section 01560-Temporary Barriers and Enclosures.

Secure all inspections required.

CLEAN-UP

Provide cleaning and ensure removal of all debris at end of each working day.  Provide final cleaning under provisions of Section 01740-Cleaning.

DEMONSTRATION

Provide demonstration of system operation under provisions of Section 01820-Demonstration and Training.

Video Taped Maintenance Demonstration:  Standard DVD format CD-Rom video of manufacturer's recommended maintenance, cleaning, and repair procedures.

END OF SECTION