# SECTION 15075 (21 05 53)

## MECHANICAL IDENTIFICATION

- GENERAL

  - SECTION INCLUDES

    - Identification of mechanical products installed under Division 15.

  - RELATED SECTIONS

    - Section 09900 - Paints and Coatings.

  - REFERENCES

    - ANSI/ASME A13.1 - Scheme for the Identification of Piping Systems.

    - FS TT-E-489F & Int AM-1 - Gloss Alkyd Enamel for Interior & Exterior Surfaces.

    - FS TT-E-508B &AM-4 - Interior Semigloss, Tints & White Enamel.

    - FS TT-E-543A & AM-1 -Interior Undercoats, Tints & White Enamel.

    - FS TT-P-30D - Odorless Alkyd Flat White Paint & Tints for Interior Surfaces.

    - FS TT-P-645 - Zinc Chromate, Alkyd Type Primer Paint.

    - FS TT-V-51F - Varnish, Asphalt.

  - SUBMITTALS

    - Submit product data under provisions of Section 01330 - Submittal Procedures.

    - Submit list of wording, symbols, letter size and color coding for mechanical identification.

    - Submit manufacturer's name and model number.

    - Submit manufacturer's installation instructions under provisions of Section 01330 - Submittal Procedures.

- PRODUCTS

  - ACCEPTABLE MANUFACTURERS

    - Seton Name Plate Co. (New Haven, CT)

    - W. H. Brady Co. (Milwaukee, WI)

  - MATERIALS

    - Color:  Unless specified otherwise, conform with ANSI/ASME A13.1.

    - Plastic Nameplates:  Laminated three-layer plastic with engraved black letters on light contrasting background color.

    - Plastic Tape Pipe Markers:  Flexible, vinyl film tape with pressure sensitive adhesive backing and printed markings.

  - COLOR CODING

    - Identify piping with markers and directional arrows as follows:

Pipe Contents	Pipe Color	Abbreviation

Domestic Cold Water	Light Green		CW

Domestic Hot Water	Light Green		HW

Compressed Air	Green	A

Chilled Water Supply	Dark Blue	CHWS

Chilled Water Return	Dark Blue	CHWR

Condenser Water Supply	Light Blue	CWS

Condenser Water Return	Light Blue	CWR

Chemical Feed	Yellow	C

Propane or Natural Gas	Yellow	G

Refrigerant Relief/Purge Piping	Yellow	R

Fire Protection Piping 	Red	F

(Exposed Piping Only)

Electrical Conduit/Controls	Red

- EXECUTION

  - PREPARATION

    - Degrease and clean surfaces to receive adhesive for identification materials.

  - INSTALLATION

    - All exposed fire protection piping in mechanical rooms shall be painted.

    - Plastic Nameplates: Install with corrosive-resistant mechanical fasteners or adhesive.

    - Plastic Tape Pipe Markers: Install complete around pipe under provisions of manufacturer's instructions.

    - Identify each AHU with a minimum 2 inch high stenciled painted, sequential numerical format indicating the building number followed by the  number and area served such as AHU-1-1/Adminstration Office, AHU-1-2/Media Center, etc.

    - Identify each exhaust fan with a minimum 2 inch high stenciled painted, sequential numerical format indicating the building number followed by the fan number, area served and the ventilation rate for which the exhaust fan was designed such as EF-1-1/Flammable Storage Room/400 CFM, etc.

    - Valves: Identify valves in main and branch piping with brass tags and chains.

    - Piping: Identify piping, concealed or exposed, with plastic tape pipe markers.  Tags may be used on small diameter piping.  Identify service, flow direction and pressure. Install in clear view and align with axis of piping. Locate identification not to exceed 20 feet on straight runs including risers and drops, adjacent to each valve and tee, at each side of penetration of structure or enclosure and at each obstruction.

    - Underground Plastic Pipe Markers:  Install yellow metallic detection tape 6 to 8 inches below finished grade, directly above exterior buried chemical piping, gas piping, chilled water and condenser water piping.

  - VALVE CHART AND SCHEDULE

    - Provide one copy of valve chart and schedule behind plexiglass or lexan.  Install at location as directed by Project Consultant.

END OF SECTION