- SECTION 15182

- HVAC PUMPS

- GENERAL

  - SECTION INCLUDES

    - Inline circulators.

    - Base mounted pumps.

  - RELATED SECTIONS

    - Section 15070 - Mechanical Sound and Vibration Control.

    - Section 15089 - Piping Insulation.

  - REFERENCES

    - ANSI/UL 778 - Motor Operated Water Pumps.

  - QUALITY ASSURANCE

    - Manufacturer: Company specializing in manufacture, assembly and field performance of pumps with minimum five years experience.

    - Alignment: Base mounted pumps shall be aligned by qualified millwright and alignment certified.

  - SUBMITTALS

    - Submit product data under provisions of Section 01330 - Submittal Procedures.

    - Submit certified pump curves showing performance characteristics with pump and system operating 	point plotted. Include NPSH curve when applicable.

    - Submit manufacturer's installation instructions under provisions of Section 01330 - Submittal Procedures.

  - OPERATION AND MAINTENANCE DATA

    - Submit operation and maintenance data.

    - Submit manufacturer’s installation instructions, lubrication instructions, assembly views and replacement parts list.

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver products to site under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

    - Store and protect products under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

    - Deliver and store products in shipping containers with labeling in place.

- PRODUCTS

  - ACCEPTABLE MANUFACTURERS

    - Armstrong.

    - Taco.

    - Bell & Gossett.

    - Fairbanks.

    - Wienman.

    - District Approved Equal.

  - GENERAL CONSTRUCTION REQUIREMENTS

    - Balance: Rotating parts, statically and dynamically balanced.

    - Construction to permit servicing without breaking piping or motor connections.

    - Pump Motor enclosures shall be Totally Enclosed Fan Cooled (TEFC) for all pump locations (indoor/outdoor).

    - Pump Connections: Flanged or screwed.

  - INLINE CIRCULATING PUMP                                                                                         (Fractional Horsepower)

    - Type: Horizontal shaft, single stage, direct connected with resiliently mounted motor for inline installation.

    - Casing: Cast iron or bronze rated for 125 PSIG maximum working pressure.

    - Impeller: Brass or bronze, keyed to shaft.

    - Bearings: Two, oil lubricated bronze sleeves.

    - Shaft: Stainless steel with stainless steel sleeve and integral thrust collar.

    - Seal: Carbon rotating against a stationary ceramic seat.

    - Drive: Flexible coupling.

  - BASE MOUNTED PUMP

    - Type: Horizontal shaft, single stage, long coupling drive, end suction, back pullout.

    - Casing: Cast iron rated for 125 PSIG maximum working pressure with suction and discharge gauge ports, seal flush connection, drain plug, flanged suction and discharge.

    - Impeller: Bronze, fully enclosed, keyed to shaft.

    - Bearings: Grease lubricated roller or ball bearings.

    - Shaft: Alloy steel with copper, bronze or stainless steel shaft sleeve.

    - Seal: Carbon rotating against a stationary ceramic seat, maximum continuous operating temperature of 225 Degree F.

    - Drive: Flexible coupling with coupling guard, Woods type.

    - Baseplate: Cast iron or fabricated steel with integral drain rim.

- EXECUTION

  - INSTALLATION

    - Install pumps under the provisions of the manufacturer's instructions.

    - Provide access space around pumps for service. Provide no less than minimum as recommended by manufacturer.

    - Ensure pumps operate at specified system fluid temperatures without vapor binding and cavitation, that they are non-overloading in parallel or individual operation and that they operate within five percent of midpoint of published maximum efficiency curve.

    - Decrease from line size with long radius reducing elbows or reducers. Support piping adjacent to pump such that no weight is carried on pump casing. For close coupled or base mounted pumps, provide supports under elbows on pump suction and discharge line sizes 4 inches and larger.

    - Provide air cock and drain connection on horizontal pump casings.

    - Provide manifold pressure gauge assembly.

    - Provide drains for bases and seals, piped to and discharging into floor drains.

    - Lubricate pumps before startup.

    - Install base mounted pumps level on concrete pad with anchor bolts and grout in place.

    - A qualified millwright shall check, align and certify base mounted pumps prior to startup.

    - Coordinate with plumbing piping and related work to achieve operating system.

    - If pump does not meet designed performance within five percent of design values, upgrade pumps at no additional cost to Owner.

- END OF SECTION