- SECTION 15184 (?? ?? ??)

- REFRIGERANT DX PIPING AND SPECIALTIES

- GENERAL

  - SECTION INCLUDES

    - Piping.

    - Refrigerant.

    - Moisture and liquid indicators.

    - Valves.

    - Strainers.

    - Check valves.

    - Pressure relief valves.

    - Filter-driers.

    - Solenoid valves.

    - Expansion valves.

    - Receivers.

    - Flexible connections.

    - Pressure switches.

    - Silver solder.

  - RELATED SECTIONS

    - Section 15060 - Hangers and Supports.

    - Section 15070 - Mechanical Sound and Vibration Control.

    - Section 15075 - Mechanical Identification.

    - Section 15089 - Piping Insulation.

    - Section 15724 - DX Air Handling Unit with Hot Gas Reheat.

    - Section 15731 - Packaged Suspended DX Air Conditioning Unit with Hot Gas Reheat.

    - Section 15732 - Packaged Rooftop DX Air Conditioning Unit.

    - Section 15733 - Packaged Grade Mounted DX Air Conditioning Unit with Hot Gas Reheat.

    - Section 15734 - Packaged EHPA Rooftop DX Air Conditioning Unit.

    - Section 15736 - Ductless Air Conditioner.

  - REFERENCES

    - ANSI/ARI 495 - Refrigerant Liquid Receivers.

    - ANSI/ARI 710 - Liquid Line Dryers.

    - ANSI/ASHRAE 15 - Safety Code for Mechanical Refrigeration.

    - ANSI/ASHRAE 34 - Number Designation of Refrigerants.

    - ANSI/ASME B16.22 -Wrought Copper and Copper Alloy Solder Joint Pressure Fittings.

    - ANSI/ASME B16.26 - Cast Copper Alloy Fittings For Flared Copper Tubes.

    - ANSI/ASME B31.5 - Refrigeration Piping.

    - ANSI/ASME B31.9 - Building Services Piping.

    - ANSI/ASTM B32 - Specification for Solder Metal.

    - ANSI/ASTM B88 - Specification for Seamless Copper Water Tube.

    - ASTM B280 - Seamless Copper Tube for Air Conditioning and Refrigeration Field Service.

    - ANSI/AWS A5.8 - Specifications for Filler Metals for Brazing and Braze Welding.

    - ANSI/AWS D1.1 - Structural Welding Code, Steel.

    - ANSI/UL 429 - Electrically Operated Valves.

    - ARI 750 - Thermostatic Refrigerant Expansion Valves.

    - ARI 760 - Solenoid Valves for Use With Volatile Refrigerants.

  - SUBMITTALS

    - Submit product data to site under provisions of Section 01330- Submittal Procedures.

    - Submit manufacturer's installation instructions under provisions of Section 01330 -Submittal Procedures.

    - Submit shop drawings indicating schematic layout of system, including equipment, critical dimensions and sizes.

    - Submit product data indicating general assembly of specialties, including manufacturers catalogue information.

    - Submit data indicating pipe sizing.

    - Submit test reports.

    - Submit Test reports indicating results of leak test, acid test.

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver products to site under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

    - Store and protect products under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

    - Protect piping and specialties from entry of contaminating material by leaving end caps and plugs in place until installation.

    - Provide for safe handling of refrigerants to prevent release into the atmosphere in compliance with EPA Clean Air Act Title VI, 608.

- PRODUCTS

  - PIPING

    - Copper Tubing: ASTM B280, Type ACR hard drawn.

      - Fittings: ANSI/ASME B16.22 wrought copper.

      - Joints:  ASTM B32 , lead free solder, 95-5 tin-antimony or tin silver with melting range of 430 to 535 Degree F or AWS A5.8, brazed, BcuP silver/ phosphorous/copper alloy with melting range of 1190 to 1480 Degree F.

    - Copper Tubing to 7/8 Inch OD:  ANSI/ASTM B88, Type K, annealed.

      - Fittings:  ANSI/ASME B16.26 cast copper, long radius.

      - Joints:  ASTM B32 , lead free solder, 95-5 tin-antimony or tin silver with melting range of 430 to 535 Degree F or AWS A5.8, brazed, BcuP silver/ phosphorous/copper alloy with melting range of 1190 to 1480 Degree F.

  - REFRIGERANT

    - Refrigerant: R-410A.

    - CFC based refrigerants are not approved.

  - MOISTURE AND LIQUID INDICATOR

    - Single port type, UL listed with copper or brass body, flared or solder ends, sight glass, color coded paper moisture indicator and plastic cap, maximum working pressure of 500 PSIG and maximum temperature of 200 Degree F.

  - VALVES

    - Packed Ball Valves: Two piece forged brass body with chrome plated ball, teflon seats, brass seal cap, neoprene ring stem seals, copper tube extension, maximum working pressure of 500 PSIG and maximum temperature of 300 Degree F.

    - Packed Angle Valves: Forged brass or nickel plated forged steel, forged brass seal caps with copper gasket, rising stem and seat with backseating, molded stem packing, solder or flared ends, maximum working pressure of 500 PSIG and maximum temperature of 275 Degree F.

  - STRAINER

    - Straight Thru Type:  Steel shell, copper plated fittings, stainless steel wire screen.

    - Straight Thru or Angle Type: Brass or steel shell, steel cap and flange, replaceable cartridge of stainless steel wire or monel reinforced with brass screen, maximum working pressure of 430 PSIG.

  - CHECK VALVE

    - Globe Type: Bronze or forged brass body, forged brass cap with neoprene seal, brass guide and disc holder, phosphor-bronze or stainless steel spring, teflon seat disc, maximum working pressure of 450 PSIG and maximum temperature of 300 Degree F.

    - Straight Thru Type: Brass body, brass disc, phosphor-bronze or stainless steel spring, neoprene seat, maximum working pressure of 500 PSIG and maximum temperature of 250 Degree F.

  - PRESSURE RELIEF VALVE

    - Straight Thru or Angle Type: Brass body and disc, neoprene seat, factory sealed, ASME stamped, National Board Certification, standard pressure setting, ANSI/ASHRAE 15 Standard selection.

  - FILTER DRIER

    - Angle Type (Replaceable Cartridge): ANSI/ARI 710, UL listed, brass shell, bronze cap, perforated brass shell and molded desiccant filter core, maximum working pressure of 350 PSIG.

    - Straight Thru Type (Permanent): ANSI/ARI 710, UL listed, steel shell with molded desiccant filter core, maximum working pressure of 400 PSIG.

  - SOLENOID VALVE

    - Valve: ARI 760, pilot operated, copper or brass body, copper or brass internal parts, synthetic seat, stainless steel stem, stainless steel plunger assembly, flared, soldered or threaded ends, maximum working pressure of 500 PSIG.  Stem shall permit manual operation in case of coil failure.

    - Coil Assembly: UL listed, replaceable, molded electromagnetic coil, moisture and fungus proof, surge protector, color coded lead wires, integral junction box.

  - METERING DEVICE (EXPANSION VALVE)

    - Angle or Straight Thru Type: ARI 750, capillary tube for under three tons or thermostatic expansion valve for three tons and larger, brass body, internal or external equalizer, adjustable superheat setting, replaceable inlet strainer.

    - Selection: Evaluate refrigerant pressure drop through system to determine available pressure drop across valve. Select valve for maximum load at design operating pressure and minimum 10 Degree F superheat.  Select to avoid being undersized at full load and excessively oversized at part load.

  - RECEIVER

    - 6 Inch I.D. and Under: ANSI/ARI 495, UL listed, steel body, brazed; 400 PSIG maximum pressure rating with lappings for inlet, outlet and pressure relief valve.

    - Over 6 Inch I.D.: ANSI/ARI 495, welded steel body, tested and stamped under provisions of Section 8D of the ANSI/ASME Boiler and Pressure Vessels Code; 400 PSIG maximum pressure rating with lappings for inlet, outlet and pressure relief valve.

  - FLEXIBLE CONNECTOR

    - Corrugated stainless steel hose with single layer of stainless steel exterior braiding, minimum 9 inches long with copper tube ends; maximum working pressure 400 PSIG.

  - PRESSURE SWITCH

    - High and low adjustable pressure switches with manual resets.

- EXECUTION

  - PREPARATION

    - Ream pipe and tube ends and remove burrs.

    - Remove dirt and scale on inside and outside before assembly.

  - INSTALLATION

    - Install specialties under provisions of the manufacturer's instructions.

    - Route piping in orderly manner with plumbing parallel to building structure and maintain gradient.

    - Install piping to conserve building space and not interfere with use of space.

    - Group piping whenever practical at common elevations and locations. Slope piping one percent in direction of oil return.

    - Install piping to allow for expansion and contraction without stressing pipe, joints or connected equipment.

    - Provide clearance for installation of insulation and access to valves and fittings.

    - Provide access where valves and fittings are not exposed.  Locate valves and metering devices in easily accessible locations having adequate clearance to service devices.

    - Scrape, brush clean and apply one coat of zinc rich primer to welding joints wherever pipe support members are welded to structural building frame,

    - Prepare pipe, fittings, supports and accessories for finish painting.

    - Use dielectric fittings or couplings for dissimilar metals.

    - Insulate piping and accessories.

    - Locate capillary tube sensing bulb immediately downstream of evaporator on suction line.

    - Provide external equalizer piping on expansion valves with refrigerant distributor connected to evaporator.

    - Install flexible connectors at right angles to axial movement of compressor.

    - Fully charge completed system with refrigerant after evacuation and testing.

    - Provide electrical connection to solenoid valves.

  - APPLICATION

    - Provide line size liquid indicators in main liquid line leaving condenser or if receiver is provided, in liquid line leaving receiver. Install moisture indicator so it can be viewed from service area.

    - Provide line size strainer upstream of each automatic valve. In addition to multiple expansion valves with integral strainers, install single main liquid line strainer.

    - Provide shutoff valves on each side of the strainer.

    - Provide replaceable cartridge filter-driers for each refrigerant circuit.  Install vertically in liquid line adjacent to receivers with a valve bypass assembly to permit isolation of driers for servicing.

    - Provide solenoid valves in liquid line of systems operating with single pump-out or pump-down compressor control.  In addition, provide in liquid line of single or multiple evaporator systems and in oil bleeder lines from flooded evaporators to stop flow of oil and refrigerant into the suction line when system shuts down.

    - Provide refrigerant charging connections (packed angle valve) in liquid line between the receiver shutoff valve and expansion valve.

    - Utilize flexible connectors at or near compressors when the piping configuration does not absorb 	vibration.

  - FIELD QUALITY CONTROL

    - Field testing will be performed under provisions of Division One.

    - Test refrigeration system in accordance with ANSI/ASME B31.5.

- Pressure test system with small amount of refrigerant and dry nitrogen at 300 PSIG. Use halide torch or electronic leak detector to check for leaks. Perform final test at 30Inches vacuum for a 24 hour period with no pressure deviation. Provide written verification of the system test to the Owner’s representative.

- END OF SECTION