# SECTION 15211 (41 65 13)

## AIR COMPRESSOR

- GENERAL

  - SECTION INCLUDES

    - Stationary and portable air compressor.

  - RELATED SECTIONS

    - Section 15060 - Hangers and Supports

    - Section 15075 - Mechanical Identification.

    - Section 15105 - Plumbing Piping.

  - REFERENCES

    - ANSI/ASME Section 8D - Boiler and Pressure Vessels Code

    - ANSI/NFPA 70 - National Electrical Code

  - QUALITY ASSURANCE

    - Provide portable air compressor with manufacturer's name, model number and capacity identified.

    - Ensure products and installation of specified products are in conformance with recommendations and requirements of the following organizations:

      - ASME

      - NEMA

      - UL

  - SUBMITTALS

    - Submit product data under provisions of Section 01330 - Submittal Procedures.

    - Submit manufacturer's installation instructions under provisions of Section 01330-Submittal Procedures.

  - OPERATION AND MAINTENANCE DATA

    - Submit operation and maintenance data under provisions of Section 01830-Operation and Maintenance.

    - Include exploded view and replacement parts lists.

- PRODUCTS

  - ACCEPTABLE MANUFACTURERS

    - Campbell Hausfeld

    - Saylor Beall

    - Ingersoll-Rand

    - Gardner Denver (Champion)

    - Quincy

  - AIR COMPRESSOR                                                                                    (Stationary/Tank Mounted)

    - Air-cooled, dual-stage, oil lubricated, belt driven reciprocating type air compressor with cast iron cylinders atop a 120 Gallon ASME coded and labeled horizontal receiver.

    - Provide unit with dry type inlet air filter/silencer, open drip-proof electric motor, dual gauge regulator, pressure gauge, safety valves, drain valve, thermal overload protection, service valve and interconnecting piping between receiver and control.

    - Piston Displacement:  102 CFM with 175 PSIG operating air pressure.

    - Normal Operating Pressure:  100 PSIG.

    - Unit rated for 25 HP, 480 V, 3 Phase, 60 Hz, 1100 RPM.

    - Model HRA25-152 manufactured by Champion

  - AIR COMPRESSOR                                                                                                         (Portable/Wheeled)

    - Air-cooled, single-stage, oil lubricated, belt driven reciprocating type air compressor with cast iron cylinders atop a 20 Gallon ASME coded and labeled horizontal receiver.

    - Provide unit with dry type inlet air filter/silencer, open drip-proof electric motor, dual gauge regulator, pressure gage, safety valves, drain valve, thermal overload protection, service valve and interconnecting piping between receiver and control.

    - Piston Displacement:  6.4 CFM with 90 PSIG operating air pressure.

    - Normal Operating Pressure:  100 PSIG.

    - Unit rated for 4 HP, 115/230 V, 1 Phase, 60 Hz, 1750 RPM.

    - Model VT619604AJ manufactured by Campbell Hausfeld.

- EXECUTION

  - INSTALLATION

    - Coordinate installation with architectural and electrical work.

END OF SECTION