# SECTION 15280 (21 07 ??)

## EQUIPMENT INSULATION

- GENERAL

  - SECTION INCLUDES

    - Emergency generator exhaust piping insulation.

    - Jackets and accessories.

  - RELATED SECTIONS

    - Section 15106 - Emergency Generator Piping.

    - Section 16231 - Emergency Standby Electrical Service System.

  - REFERENCES

    - ASTM C533 - Calcium Silicate Block and Pipe Thermal Insulation.

    - ASTM E84 - Surface Burning Characteristics of Building Materials.

  - QUALITY ASSURANCE

    - Applicator: Company specializing in piping insulation application with three years minimum experience.

    - Materials: Flame spread/smoke developed rating of 25/50 under provisions of ASTM E84.

  - SUBMITTALS

    - Submit product data under provisions of Section 01330 - Submittal Procedures.

    - Include product description, list of materials and thickness for each service and locations.

    - Submit manufacturer's installation instructions under provisions of Section 01330 - Submittal Procedures.

    - PRODUCTS

  - ACCEPTABLE MANUFACTURERS - INSULATION

    - Barrington Chemical Corp. (Harrison, NY).

    - Noah Technologies Corp. (San Antonio, TX).

    - Spectrum Chemical Mfg. Corp. (Gardena, CA).

    - Westco Chemical, Inc. (North Hollysood, CA).

  - INSULATION

    - Hydrous Calcium Silicate:  For the emergency generator exhaust piping.

      - Pipe:

        - ASTM C533, molded, asbestos free, noncombustible, hydrous calcium silicate equipment insulation with insulating cement compatible with insulation..

        - Maximum Water Vapor Transmission Rating: 0.20 perm.

        - ‘K' value of 0.40 at 250 Degree F.

        - Equivalent to Owens-Corning 25ASJ/SSL

  - ACCESSORIES

    - Adhesives: Water base, fire resistive, non-toxic and compatible with insulation.  Petroleum-base products are PROHIBITED.

    - Insulating Cement:  ANSI/ASTM C195; hydraulic setting mineral wool.

    - Finishing Cement:  ASTM C449.

    - EXECUTION

  - PREPARATION

    - Do not apply insulation until all surfaces to be covered are clean and dry and all foreign materials such as oil, grease, rust, scale and dirt have been removed.

    - Apply clean and dry insulation only.

    - Repair separation of joints or cracking of insulation due to thermal movement of poor workmanship.

END OF SECTION