- SECTION 15320

- FIRE PUMP AND CONTROLS

- GENERAL

1.1	SECTION INCLUDES

A.	Fire pump, jockey pump.

B.	Controls including necessary accessories as shown in the plans, specification and as required by NFPA 20.

1.2	RELATED SECTIONS

A.	Section 13851 - Fire Alarm System.

- Section 15300 - Fire Protection System.

1.3	REFERENCES

    - Florida Building Code.

    - American Society for Testing and Materials (ASTM).

    - American National Standards Institute (ANSI).

    - Factory Mutual (FM).

E.	NFPA 13 - Installation of Sprinkler Systems.

- NFPA 20 - Stationary Pumps for Fire Protection.

- NFPA 70 - National Electric Code.

- Underwriters Laboratories (UL).

1.4	QUALITY ASSURANCE

A.	Fire protection equipment and devices shall be UL listed or FM approved for service intended.

B.	Install according to NFPA 20, NEC requirements and local code regulations.

1.5	SUBMITTALS

A.	Submit product data under provisions of Section 01330 - Submittal Procedure.

B.	Submit manufacturer’s installation instructions under provisions of Section 01330 -Submittal Procedure.

C.	Submit properly identified manufacturer’s literature before starting work.

D.	Shop Drawings:  Submit detailed plans for installation of the fire pump and accessories, jockey pump, control panels and devices and all other necessary accessories

- PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS - FIRE PUMP

A.	Fairbanks

B.	Peerless

C.	Patterson

  - ACCEPTABLE MANUFACTURER - JOCKEY PUMP

- Fairbanks

- Burks

2.2	FIRE PUMP

A.	UL listed and FM approved automatic centrifugal pump complete with motor, controller and accessories capable of delivering not less than 150 percent of rated capacity at not less than 65 percent of rated pressure with characteristics as shown in the plans.

B.	Pump:  Centrifugal, horizontal split case, single stage casing with renewable bronze,      cases wearing rings and impeller wearing rings, steel shaft with renewable bronze or stainless steel sleeves, grease lubricated ball bearings, lubrication fittings, minimum suction pressure of 20 PSIG.

C.	Provide required UL accessories including:

      - Discharge manifold.

      - Automatic air release valve.

      - Suction and discharge pressure gages.

      - Suction and discharge tapered reducers.

      - Circulation relief valve.

D.	Motors shall be listed for fire pump service:

      - Horizontal open drip-proof grease lubricated, ball bearing squirrel cage and induction type with non-overloading characteristics at any point of the curve.

      - Pump and motor shall be mounted on a cast iron drip rim base plate.  Motor mounting bracket on machined pump shall be completely aligned.

E.	Transfer Switch Fire Pump Controller:

      - Design and build according to the latest edition of NFPA 20.

      - The fire pump controller and builtin automatic transfer switch shall have to withstand current rating of at least 100,000 RMS symmetrical amps on the normal power supply.

F.	The power transfer switch and fire pump controller shall be factory assembled, wired and tested.

      - Controller and transfer switch shall be in an NEMA Type 12 enclosure with floor mounting legs.  The power transfer switch shall include a disconnect/isolating switch capable of interrupting the motor locked rotor current.

      - Controller shall be of the primary resistor or reactor reduced voltage type with a combined automatic/manual start and manual/timed automatic stop.  Use reactor type when facility has a generator set.

      - Controller shall have the following required accessories:

- Pressure switch for automatic starting.

- “Power-On” pilot light indicating breaker closed and power available.

- Pressure recorder, not AC power dependent, with 7-day charts.

- Power monitor for phase failure and phase reversal.

- START/STOP push buttons for manual operation.

- Timing relay for reduced voltage starting.

- Relays with normally open (N.O.) and normally closed (N.C.) dry contacts for pump running, power failure and phase reversal.

- Failed to start relay with N.O. and N.C. dry contacts.

- Automatic stop timer set at 10 minutes, with provision to change manual shutdown only.

- Transfer switch operation and accessories shall be in accordance with NFPA 20.

- Provide extra N.O. dry contact for pilot light indicating pump running at central control station.

      - Wiring of controller, transfer switch and alarms shall be as manufactured by Firetrol, Joyslyn-Clark or Master Control.

- 2.2	JOCKEY PUMP

A.	Close coupled, turbine pump with bronze impeller and mechanical seal.  Characteristics as shown in the plans.

B.	Controller:  UL listed, main disconnect, fuse block with power fuses across the line   started, H.O.A selector switch, minimum run period timer, pressure switch in NEMA 12 cabinet.

C.	Test header in accordance with NFPA 20.

- EXECUTION

3.1	INSTALLATION

A.	Provide pump concrete foundations of size not less than the weight of the pumps or as shown in the plans.

B.	Check pump and motor on foundation for misalignment.

3.2	FIELD QUALITY CONTROL

A.	Factory test each pump for performance data and compliance with specifications.

B.	Hydrostatically test pump for not less than 5 minutes.  Test pressure to be 150 percent of pump working pressure but not less than 250 PSI.

C.	Pump casings shall be tight with joists leakproof.

D.	Furnish NFPA 20 pump acceptance test data.  Test data form shall be as shown in NFPA 20, Figure A-11-2.6.3(f).  Tests shall be conducted according to the requirements of NFPA 20.

END OF SECTION