# SECTION 15719 (23 77 00)

## MULTIZONE AIR HANDLING UNIT

- GENERAL

  - SECTION INCLUDES

    - Packaged central station chilled water multizone air handling unit.

  - RELATED SECTIONS

    - Section 15070 - Mechanical Sound and Vibration Control.

    - Section 15083 - Duct Insulation.

    - Section 15810 - Ducts.

    - Section 15825 - Electric Duct Heater.

    - Division 16 - Electrical.

  - REFERENCES

    - AMCA 99 - Standards Handbook.

    - AMCA 210 - Laboratory Methods of Testing Fans for Rating Purposes.

    - AMCA 300 - Test Code for Sound Rating Air Moving Devices.

    - ARI 410 – Forced Circulation Air-Cooling and Air-Heating Coils.

    - ARI 430 - Standard for Central Station Air Handling Units.

    - ARI 435 - Standard for Application of Central Station Air Handling Units.

    - ANSI/ASHRAE 90.1 - Energy Conservation in New Building Design.

    - ANSI S12.60 - Acoustical Performance Criteria, Design Requirements & Guidelines for Schools.

    - SMACNA - Low Pressure Duct Construction Standards.

  - QUALITY ASSURANCE

    - Air Coils: Certify capacities, pressure drops and selection procedures in accordance    with ARI 410.

    - Multizone Air Handling Unit: Product of a manufacturer regularly engaged in production of components that issues complete catalog data on total product.

  - SUBMITTALS

    - Submit shop drawings and manufacturer's installation instructions under provisions of Section 01330 - Submittal Procedures.

    - Shop drawings shall indicate assembly, unit dimensions, weight loading, required clearances, construction details and field connection details.

    - Product data shall indicate dimensions, weights, capacities, ratings, fan performance, acoustical data, motor electrical characteristics, gauges and finishes of materials.

    - Submit electrical requirements for power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring.

  - OPERATION AND MAINTENANCE DATA

    - Submit operation and maintenance data under provisions of Section 01330 - Submittal Procedures.

    - Include instructions for lubrication, filter replacement, motor and drive replacement, spare parts lists and wiring diagrams.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver products to site under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements in factory-fabricated protective containers with factory-installed shipping skids and lifting lugs.

    - Store and protect products under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

    - Store in clean dry place and protect from weather and construction traffic.  Handle carefully to avoid damage to components, enclosures and finish.

  - ENVIRONMENTAL REQUIREMENTS

    - Do not operate units for any purpose, temporary or permanent, until ductwork is clean, filters are in place, bearings lubricated and fan has been test run under observation.

  - EXTRA STOCK

    - Provide one set of 4 inch depth, 80-85 percent atmospheric dust spot (ADS) efficiency, MERV 13 minipleated air filters in accordance with the latest edition of AHSRAE 52.2.

  - WARRANTY

    - Provide manufacturer's one year parts and labor warranty for the unit’s components and an extended four year parts and labor warranty on the compressor and motor.

- PRODUCTS

  - ACCEPTABLE MANUFACTURERS

    - Trane

    - Carrier

  - MULTIZONE AIR HANDLING UNIT

    - Factory assembled and pre-wired draw-thru type multizone air handling unit suitable for low (constant air volume) operation and consisting of a fan section, cooling and heating coil section, mixing box section, base rail, filter section and accessories.

    - Factory test multizone air handling unit of size, capacity and configuration as indicated and specified.

    - Base multizone air handling unit performance on sea level conditions.

    - The final equipment location and selection design must comply with the maximum noise criteria levels specified in Section 15070 – Mechanical Sound and Vibration Control, paragraphs 2.3(E) thru (J) for the dining room and other adjacent spaces.

    - The unit shall achieve a maximum background noise level from heating, ventilating and air conditioning (HVAC) systems in the dining room of 45 dBA.  Design spaces to include sufficient sound absorptive finishes for compliance with reverberation time requirements as specified in ANSI Standard S12.60-2002, Acoustical Performance Criteria Design Requirements and Guidelines for Schools.

  - CASING

    - Construct casing and removable panels of 18 gauge, double-wall galvanized steel on channel base.  Casing to be constructed and reinforced to withstand the maximum fan pressures developed.  Fabricate channel base of galvanized welded steel.

    - Casing shall include insulated, hinged, double wall access doors in the filter, fan and coil sections.

    - Insulate casing sections with 1 inch thick rigid foam insulation sandwiched between the outer milled galvanized steel wall and the inner galvanized steel wall.  Minimum insulation R-value of 5.0.

    - Construct drain pan from insulated, 20 gauge, double wall stainless steel pitched and positioned under the evaporator end plates to avoid shifting.  It shall be silver solder welded and fitted with a minimum 1 inch male pipe thread (MPT) non-corrosive drain connection and an internal P-trap.

    - The manufacturer shall be responsible for providing additional rigid board type insulation to prevent the air handling unit from sweating under the encountered operating conditions.

  - SUPPLY FAN

    - Provide fan section with forward curved, double width, double inlet centrifugal type fan.

    - Provide self-aligning, grease lubricated ball or roller bearings in pillow block cast iron housings.  Grease ball bearings or ANSI/AFBMA standards, L-50 life at 200,000 hours, pillow block type, self-aligning, grease lubricated roller bearings.  All bearings shall be provided with extended grease lines to the exterior of the unit casing with copper tube and “zerk” fitting rigidly attached to casing to allow lubrication from outside the unit casing.  The operating range of the bearings shall be from -4 Degree F to +176 Degree F.

    - Internally mount fan and motor on a welded steel base coated with zinc chromate. Factory mount motor on slide rails for accessibility.  Provide access to motor, drive and bearings through hinged access doors.

    - Provide motor and fan with internal vibration isolators.

  - MOTORS AND DRIVES

    - Motors: Maximum horsepower as indicated and specified, but not to exceed 20 HP.  Protect motor against contact failure, loss of any phase (single phasing), low voltage, high voltage, voltage unbalance, phase reversal and winding for specified voltage having a minimum power factor of 85 to 100 percent and a minimum efficiency of  91.7 percent at 100 percent load as per IEEE Test Procedure 112, Method B.  Refer to Section 15055 - Motors.

    - Motor shall be TEFC, Class B insulated and designed for continuous operation in 40 Degree C environment and a temperature rise under provisions of ANSI/NEMA MG 1 limits for insulation class, service factor and motor enclosure.

    - Shaft: Solid hot rolled steel, ground and polished with keyway and protectively coated with lubricating oil.

    - V-Belt Drive: Cast iron or steel sheaves, dynamically balanced, bored to fit shaft and keyed. Variable and adjustable pitch sheave for motors 15 HP and under selected so that the required RPM is obtained with the sheave set at mid-position; fixed sheave for 20 HP and larger, matched belts and drive rated as recommended by the manufacturer or a minimum of 1.5 times the motor rating.

    - Belt Guard: Fabricate to SMACNA Low Pressure Duct Construction Standards of 12 gauge, 3/4 inch diamond mesh wire screen welded to steel angle frame or equivalent and prime coated.  Secure to fan or fan support without short circuiting vibration isolation with provision for adjustment of belt tension, lubrication and use of tachometer with the guard in place.

  - CHILLED WATER COIL

    - Provide coil section with access to both sides of coil.  Enclose coil with headers and return bends fully contained within casing.  Slide coil into air handling unit casing through removable end panels with blank-off sheets and sealing collars at connection penetrations.

    - Provide coil fabricated of seamless drawn copper.  The inner tubing shall be rifled to produce turbulent refrigerant flow in order to enhance the heat transfer process.  The copper tubes shall be hydraulically expanded onto the aluminum fins to form a permanent metal-to-metal bond for maximum heat transfer.

    - Provide drain pan and downspouts for cooling coil banks of more than one coil high. Coils to be of sufficient free area and not incorporate moisture eliminators or coatings to prevent water carryover.

    - Provide coils indicated for water cooling. Ensure face velocity does not exceed 500 FPM.

    - Coil to contain a minimum of six rows and a maximum of 8 to 12 Fins per Inch (FPI).

    - Coil to be pressure tested to 420 PSIG of nitrogen.

  - HEATING COIL

    - Provide coil section with access to both sides of coil.  Enclose coil with headers and return bends fully contained within casing.  Slide coil into air handling unit casing through removable end panels with blank-off sheets and sealing collars at connection penetrations.

    - Provide coil fabricated of seamless drawn copper.  The inner tubing shall be rifled to produce turbulent flow in order to enhance the heat transfer process.  The copper tubes shall be hydraulically expanded onto the aluminum fins to form a permanent metal-to-metal bond for maximum heat transfer.

    - Provide coils indicated for water heating. Ensure face velocity does not exceed 960 FPM.

    - Coil to contain a minimum of one row and a maximum of 8 to 12 Fins per Inch (FPI).

    - Coil to be pressure tested to 420 PSIG of nitrogen.

  - PRESSURE INDEPENDENT CHARACTERIZED CONTROL VALVE (PICCV)

    - Refer to Section 15900 - HVAC Instrumentation and Controls for New & Phased Replacement Facilities.

  - FILTER SECTION

    - Provide flat type filter section constructed of galvanized steel and containing filter guides and hinged access doors on both sides for side loading of filters.

    - Provide 4 inch depth filter section, UL Class 2, high efficiency, 80-85 percent     atmospheric dust spot (ADS), disposable MERV 13 minipleated type air filters.  Refer to Section 15860 - Air Cleaning Devices.

    - Provide an analog differential pressure gauge across the filter to monitor dirty filter conditions.

  - LOUVERS (EXTERIOR WALL)

    - Refer to Section 10200 - Louvers and Vents.

  - DAMPER ACTUATORS

    - Refer to Section 15810 - Ducts or Section 15816 - Non-Metal Ducts.

  - CONTROLS

    - Provide temperature/humidity controls consisting of the following:

      - Microprocessor based return air temperature controller with return air transmitter.

      - Field installed supply air sensor, discharge air reset sensor and a duct mounted humidistat.

  - EQUIPMENT CONDENSATE DRAIN PIPING

    - Refer to Section 15183 - Hydronic Piping.

- EXECUTION

  - INSTALLATION

    - Install air handling unit under provisions of the manufacturer's instructions.

    - Mechanical rooms shall be of sufficient size to provide the HVAC equipment     manufacturer's recommended clearances for maintenance and servicing.  A MINIMUM OF THREE FEET CLEARANCE SHALL BE PROVIDED ON BOTH SIDES AND FRONT OF THE AHU AND TWO FEET CLEARANCE IN THE REAR.

    - Coordinate with the structural engineer and install the AHU on 6 inch concrete housekeeping pads in the mechanical rooms.  The pads shall extend a maximum of 4 inches beyond the foot[print of the supported equipment in all directions and have 1/2 inch chamfered edges.

    - When the AHUs are provided with a minimum 6 inch factory installed base rails, the use of the 6 inch concrete pads shall not be required.

    - AHU shall be installed on a 3/8” cross-ribbed, oil-resistant, resilient neoprene mounting pad between the unit and the base rail.

    - Route AHU copper condensate pipe to discharge into the mechanical room floor drain or safewaste (via a 2” minimum air gap) that is connected to the floor drain and routed into the sanitary system.  Floor drain shall be installed immediately adjacent to the 6 inch housekeeping concrete pad.  Should connection to the sanitary system not be possible, provide a floor drain with a backwater valve and connect the condensate into the site storm drain system catch basin only after approval by the SBBC Facilities Design & Support Section.  Floor drains installed in front of the AHU where they can become a tripping hazard are PROHIBITED.

    - Install spring type vibration isolators between the AHU and the 6 inch concrete housekeeping pad if the AHU fan is not provided with internal spring isolation.  Otherwise, install the AHU on a 3/8 inch cross-ribbed neoprene mounting pads.

    - Provide 6 inch long flexible duct connectors at all duct connections to rotating or vibrating equipment.  Refer to Section 15810 - Ducts.

    - Connect chilled water and heating water piping to the AHU so that it is clear of access doors, filters, motor and coil pull area.  It’s preferable that the chilled water and heating water piping be installed behind or to the side of the unit to allow side access to the unit.

    - During construction, seal the AHU inlet and outlet openings with polyethylene sheet to prevent construction dust and debris from entering AHU.  Verify that during construction, the AHU is fitted with 4 inch depth, MERV 13 efficiency air filters.

    - Prior to startup, thoroughly clean inside of AHU of all construction dust and debris.

    - Do not operate AHU until mechanical room has been cleaned and filters are in place.

    - Provide an analog type differential pressure gauge across the filters to monitor pressure conditions across the filters.

    - All new AHUs shall be tagged and identified in a sequential format.

    - Identify AHUs with a minimum 2 inch high stenciled painted, sequential numerical format indicating the building number followed by the equipment number and the area or zone  served such as AHU-1-1/Administration Office, AHU-1-2/Media Center, etc.

  - TEST AND ADJUST

    - Start equipment in the presence of the AHU manufacturer’s representative.  Test the unit to demonstrate proper operation at performance requirements specified including running balance, belt slippage, generated noise, proper heating, adequate air flow and unusual or similar indication of improper operation.

    - Subsequent to test and balance, remove the filters installed during construction and replace with a new set of MERV 13 efficiency air filters.

    - If sweating occurs on the casing, provide additional foil faced, rigid board insulation of sufficient thickness to be installed on the casing exterior to eliminate the sweating.

    - Correct any other deficiencies in the AHU operation.

END OF SECTION