# SECTION 15720 (23 77 00)

## AIR HANDLING UNIT

GENERAL

SECTION INCLUDES

Packaged central station chilled water air handling unit.

RELATED SECTIONS

Section 15070 - Mechanical Sound and Vibration Control.

Section 15083 - Duct Insulation.

Section 15810 - Ducts.

Section 15816 - Non-Metal Ducts.

Section 15825 - Electric Duct Heater.

Section 15900 - HVAC Instrumentation and Controls.

Division 16 - Electrical.

REFERENCES

AMCA 99 - Standards Handbook.

AMCA 210 - Laboratory Methods of Testing Fans for Rating Purposes.

AMCA 300 - Test Code for Sound Rating Air Moving Devices.

AMCA 611 - Certified Ratings Program, Airflow Measurement Program.

ARI 260 - Sound Rating of Ducted Air Moving and Conditioning Equipment.

ARI 410 - Forced-Circulation Air-Cooling and Air-Heating Coils.

ARI 430 - Standard for Central-Station Air Handling Units.

ARI 435 - Standard for Application of Central Station Air Handling Units.

ANSI/ASHRAE 52.2 - Method of Testing General Ventilation Air Cleaning Devices for     Removal Efficiency by Particle Size.

ANSI/ASHRAE 62.1 - Ventilation for Acceptable Indoor Air Quality.

ANSI/ASHRAE 90.1 - Energy Standard for Buildings Except Low Rise Residential Buildings.

ASHRAE 111 - Measurement, Testing, Adjusting and Balancing of Building HVAC Systems.

SMACNA - Low Pressure Duct Construction Standards.

QUALITY ASSURANCE

Air Coils: Certify capacities, pressure drops and selection procedures in accordance    with ARI 410.  Unit shall be provided with a certification label affixed to it.

Air Handling Units: Product of a manufacturer regularly engaged in production of components that issues complete catalog data on total product.  Unit shall be manufactured to conform to UL 1995 and shall be listed by either UL or CUL.  Unit shall be provided with listing agency label affixed to it.

Air handling unit to be certified in accordance with ARI 430.

Airflow Monitoring Station:  Airflow measurement station to be certified in accordance with AMCA 611 and shall be licensed to bear the AMCA Seal.

SUBMITTALS

Submit shop drawings and manufacturer's installation instructions under provisions of Section 01330 - Submittal Procedures.

Shop drawings shall include a plan and elevation view of the assembly, unit dimensions, weights, capacities, ratings, fan performance, acoustical data, motor electrical characteristics, lift points, gauges and finishes of materials, required clearances, construction details and field connection details.

Submit electrical requirements for power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring.

An electrical schedule shall be provided for each electrical circuit to which field-installed power must be supplied.  Schedule to include unit tag identification, circuit description, voltage/phase/hertz, minimum circuit ampacity (MCA) and calculated maximum overcurrent protection (MOP).

OPERATION AND MAINTENANCE DATA

Submit operation and maintenance data under provisions of Section 01330 - Submittal Procedures.

Include instructions for lubrication, filter replacement, motor and drive replacement, spare parts lists and wiring diagrams.

DELIVERY, STORAGE AND HANDLING

Deliver products to site under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements in factory-fabricated protective containers with factory-installed shipping skids and lifting lugs.

Products shall be fully assembled to practical shipping and rigging limitations from the manufacturer.  Products not shipped fully assembled shall have tags and airflow arrows on each section to indicate location and orientation in direction of airflow.  Shipping splits shall be clearly defined on the submittal drawings.  Cost associated with                     non-conformance to shop drawings shall be the responsibility of the manufacturer.

Product shall be delivered to the jobsite with the fan motors, sheaves and belts completely assembled and mounted.

Store and protect products under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

Store in clean dry place and protect from weather and construction traffic.  Handle carefully to avoid damage to components, enclosures and finish.

ENVIRONMENTAL REQUIREMENTS

Do not operate units for any purpose, temporary or permanent, until ductwork is clean, filters are in place, bearings lubricated and fan has been test run under observation.

EXTRA STOCK

Provide one set of 4 inch depth, 80-85 percent atmospheric dust spot (ADS) efficiency, MERV 13 minipleated air filters in accordance with the latest edition of AHSRAE 52.2.

PRODUCTS

ACCEPTABLE MANUFACTURERS

Trane

Carrier

York

Daikin

AIR HANDLING UNIT

Factory assembled and pre-wired draw-thru type stacked air handling unit suitable for low (constant air volume) or medium pressure (variable air volume) operation and consisting of a fan section, coil section, mixing box section, outside air cooling section or stacked dehumidification unit (SDU) for constant air volume systems, flat filter section, base rail if applicable, filter section and accessories.  For constant air volume systems only, provide a face and bypass damper section should the outside air cooling section or SDU design concept not be possible.

The integral factory base, supporting all sections of the unit, shall be of sufficient height for proper trapping.  Base rails not constructed of galvanized steel shall be chemically cleaned and coated with both a rust-inhibiting primer and a finished coat of rust-inhibiting enamel.

Factory test air handling units of sizes, capacities and configuration as indicated and specified.

Base air handling unit performance on sea level conditions.

The final equipment location and selection design must comply with the maximum noise criteria levels specified in Section 15070 - Mechanical Sound and Vibration Control, paragraphs 2.3(E) thru (J) for classroom and other core learning spaces.

The unit shall achieve a maximum background noise level from heating, ventilating and air conditioning (HVAC) systems in classrooms and other core learning spaces of 45 dBA.  Design classrooms and other core learning spaces to include sufficient sound absorptive finishes for compliance with reverberation time requirements as specified in ANSI Standard S12.60-2002, Acoustical Performance Criteria Design Requirements and Guidelines for Schools.

CASING

Construct casing of 18 gauge, 2 inch double-wall galvanized steel on a galvanized welded steel channel base and include insulated, hinged, double wall access doors in the filter, fan and coil sections.

Casing to be constructed and reinforced to withstand the maximum fan pressures developed.  Access panels or access doors removal shall not affect the structural integrity of the unit.   Contractor shall be responsible to provide connection flanges and all other framework that is required to properly support the unit.

Casing air leakage shall not exceed Leak Class 6 at specified casing pressure in accordance with ASHRAE 111 where the Maximum Casing Leakage (CFM/100 SF of casing surface area) = CL x p.065.

Air leakage shall be determined at a casing static pressure of 8 Inches W.G.  Specified air leakage shall be accomplished without the use of caulking.  Total estimated air leakage shall be reported for each unit in CFM as a percentage of supply air and as an ASHRAE 111 Leakage Class.

Casing wall, roof and floor panels along with access doors shall be with minimum insulation R-value of 13 sandwiched between the outer milled galvanized steel wall and the inner galvanized steel wall.

Casing panel inner liners shall not extend beyond the unit exterior nor be in contact with the exterior frame.  A mid-span interior thermal break shall b provided on all casing panels.

DRAIN PAN

Construct drain pan from insulated, double wall stainless steel with welded corners and a bottom drain designed in accordance with ASHRAE 62.1.

Drain pan shall be of sufficient size to collect all condensation produced by the cooling coil, be sloped in two planes and pitched to drain connections so as to promote positive drainage in order to eliminate stagnant water conditions when the unit is installed level and trapped as per the manufacturer’s requirements.

The drain pan threaded outlet connection shall be external of the unit, located at the lowest point of the drain pan and be of sufficient diameter to preclude drain pan overflow under any normally expected operating conditions.  Threaded outlet connections under the unit floor are PROHIBITED.

Drain connections shall be fabricated of the same material as the primary drain pan and extend a minimum of 2-1/2 inches beyond the unit base to ensure adequate room for field piping of the condensate traps.

The unit shall be installed level, trapped in accordance with the manufacturer’s requirements and visually inspected to ensure proper condensate drainage.

ACCESS DOORS

Construct 2 inch insulated, double-wall access doors with outer milled galvanized steel wall and inner galvanized steel wall.

Access doors located downstream of cooling coils shall be provided with thermal break construction at door panel/door frame interface.

Access doors shall be hinged and removable without the use of specialized tools.

A single door handle shall be provided for each door linking multiple latching points necessary to maintain the specified air leakage integrity of the unit.

Hinges shall be interchangeable with the door handle hardware to allow for alternating the door swing in the field in order to minimize access interference due to unforeseen job site obstructions.

Door hardware to be surface mounted to prevent through-casing penetrations.

Door handle shall be designed to prevent unintended door closure, be adjustable and visually indicate locking position of door latch external to the section.

Door height shall be a minimum 60 inches high when sufficient section height is available or the maximum height allowed by the unit height.

The fan section access door shall be provided with a shatterproof window.

Gasketing to be provided around the full door perimeter to prevent air leakage.

FAN

Provide fan section of the type and class shown on the Schedule.  Fan shaft shall be solid hot rolled steel, coated with a rust-inhibiting coating and properly designed so that the fan shaft does not pass through the first critical speed as it comes up to the rated RPM.  Fan shall be statically and dynamically tested as an assembly by the manufacturer for vibration and alignment at the operating RPM to meet the design requirements.  Fans controlled by variable frequency drives (VFD) shall be statically and dynamically tested for vibration and alignment at speeds varying between 25 to 100 percent of the design RPM.  The fan wheels shall be keyed to the fan shafts to prevent slippage.

Fan shall be provided with self-aligning, grease lubricated anti-friction ball or roller bearings selected for L-50 average life at 200,000 Hours in accordance with AANSI/AFBMA 9.  Lubrication lines shall extend to the exterior drive side of the fan casing onto a support bracket containing the rigidly attached “zerk” fittings.

Fan and internally mounted motor shall be mounted on a welded steel isolation base coated with zinc chromate. Fan and motor shall be internally isolated with spring isolators.  Factory mount motor on slide rails for accessibility.  A flexible connection shall be installed between the fan and AHU to ensure complete isolation complying with NFPA 90A and UL181 requirements.  External isolation shall be furnished by the installing Contractor to avoid transmission of noise and vibration through the ductwork and building structure.

Provide fan section with access to motor, drive and bearings through hinged access doors to allow inspection and maintenance of the fan, motor and drive components.

MOTORS AND DRIVES

Motors: Maximum horsepower as indicated and specified, but not to exceed 20 HP.  Protect motor against contact failure, loss of any phase (single phasing), low voltage, high voltage, voltage unbalance, phase reversal and winding for specified voltage having a minimum power factor of 85 to 100 percent and a minimum efficiency of 91.7 percent at 100 percent load as per IEEE Test Procedure 112, Method B.  Refer to Section 15055 - Motors.

Variable Frequency Drive:  UL listed complying with the latest standards of ANSI, IEEE, NEC and suitable for controlling NEMA Design B motors on continuous duty in variable speed applications.  The VFD shall be capable of a minimum interruption capacity of 50,000 Ampere (AIC). Refer to Section 15052 - Variable Frequency Drive.

Design for continuous operation in 40 Degree C environment and for temperature rise under provisions of ANSI/NEMA MG 1 limits for insulation class, service factor and motor enclosure.

Bearings: ANSI/AFBMA 9, L-50 average life at 100,000 Hours, heavy duty pillow block type, self-aligning, Grease lubricated ball bearings or ANSI/AFBMA 11, L-10 average life at 120,000 Hours, pillow block type, self-aligning, grease lubricated roller bearings.  All bearings shall be provided with extended grease lines to allow lubrication from outside the AHU casing.

Shaft: Solid hot rolled steel, ground and polished with keyway and protectively coated with lubricating oil.

V-Belt Drive: Cast iron or steel sheaves, dynamically balanced, bored to fit shaft and keyed. Variable and adjustable pitch sheave for motors 15 HP and under selected so that the required RPM is obtained with the sheave set at mid-position; fixed sheave for 20 HP and larger, matched belts and drive rated as recommended by the manufacturer or a minimum of 1.5 times the motor rating.

Belt Guard: Fabricate to SMACNA Low Pressure Duct Construction Standards of 12 gauge, 3/4 inch diamond mesh wire screen welded to steel angle frame or equivalent and prime coated.  Secure to fan or fan support without short circuiting vibration isolation with provision for adjustment of belt tension, lubrication and use of tachometer with the guard in place.

Fan motor power wires shall be run in UL listed flexible metal conduit (FMC) from motor terminal housing to external motor junction box casing penetration. FMC shall be of adequate length to allow for fan belt adjustments and prevent fan vibration isolation restrictions. FMC shall be installed per NEC Article 348.

EVAPORATOR COIL & OUTSIDE AIR PRE-COOLING COIL

Provide coil section with access to both sides of coil to allow for removal and replacement without impacting the structural integrity of the AHU.  Slide coil into air handling unit casing through removable end panels with blank-off sheets and sealing collars at connection penetrations.

Coils shall be fabricated with plate fins to mimimize water carryover and maximize airside thermal efficiency.  Fin tube holes shall have drawn and bell collars to maintain consistent fin spacing to ensure performance and air pressure drop across the coils as scheduled.  Tubes shall be mechanically expanded and bonded to fin collars for maximum thermal conductivity.  Use of soldering or tinning during the fin-to-tube bonding process is not acceptable due to the inherent thermal stress and possible loss of bonding at that joint.

Enclose coil with headers and return bends fully contained within unit casing to ensure that any condensate that forms on the header or return bends shall be captured by the drain pan located under the coil

Coil casing shall be constructed of stainless steel.  End supports and tube sheets shall have bell tube holes to minimize wear of the tube wall during thermal expansion and contraction of the tube.

All coils shall be completely cleaned prior to installation into the AHU.  The fin bundle shall be degreased and steam cleaned in the direction of the airflow to ensure removal of lubricants used in the manufacturing of the fins or dirt that may have accumulated during the process.

An intermediate drain pan and downspouts shall be provided for cooling coil banks of more than one coil high.  The intermediate drain pan shall be located between each coil,  designed to be of sufficient size to collect all condensation produced from the coil, sloped to promote positive drainage and ensure the elimination of stagnant water conditions.

The intermediate drain pan shall begin at the leading face of the water producing device and be of sufficient length extending downstream to prevent condensate from passing through the airstream of the lower coil.

The downspouts on the intermediate drain pan shall direct the condensate to the primary drain pan.  The intermediate drain pan outlet shall be located at the lowest point of the pan and shall be of sufficient diameter to preclude drain pan overflow under any normally expected operating condition.

Hydronic Coils

The supply and return header connections shall be clearly labeled on the unit exterior such that the direction of the coil water flow is counter to the direction of the airflow.

Coils shall be proof tested to 300 PSIG and leak tested to 200 PSIG air pressure underwater.

Headers shall be constructed of round copper pipe or cast iron.

Tubes shall be 1/2 inch O.D., minimum 0.016 inch thick copper.  Fins shall be aluminum.

Refrigerant Cooling Coils

Refrigerant suction and liquid connections shall be clearly labeled on the unit

exterior.

Coils shall be proof tested to 450 PSIG and leak tested to 300 PSIG air pressure underwater.  After testing, tube interior shall be dried, charged with dry nitrogen and sealed to prevent contamination.

Refrigerant suction and liquid headers shall be constructed of copper tubing.  Suction and liquid connections shall penetrate the unit casing to allow for sweat connections to the refrigerant lines.

Tubes shall be 1/2 inch O.D., minimum 0.016 inch thick copper.  Fins shall be aluminum.

Coils shall have equalizing type vertical distributors sized in conjunction with the coil capacity.

Hydronic coils shall be supplied with factory installed drain and vent piping to the unit exterior.

Provide coils indicated for water cooling. Ensure face velocity does not exceed 500 FPM.

Construct coils of 1/2 inch minimum copper tubes mechanically expanded into      aluminum fins.

Coil to contain a minimum of six rows and a maximum of 8 to 12 Fins per Inch (FPI).

PRESSURE INDEPENDENT CHARACTERIZED CONTROL VALVE (PICCV)

Refer to Section 15900 - HVAC Instrumentation and Controls for New & Phased Replacement Facilities.

FILTER SECTION

Provide flat type filter section constructed of galvanized steel and containing filter guides and hinged access doors on both sides for side loading of filters.

Provide 4 inch depth filter section, UL Class 2, high efficiency, 80-85 percent     atmospheric dust spot (ADS), disposable MERV 13 minipleated type air filters.  Refer to Section 15860 - Air Cleaning Devices.

Provide an analog differential pressure gauge across the filter to monitor dirty filter conditions.

FACE AND BYPASS SECTION                                                                                                   (Constant Volume Systems Only)

Provide factory mounted face and bypass dampers of the air-foiled, opposed galvanized steel blade type with metal compressible jamb seals, extruded vinyl blade edge seals and stainless steel sleeve bearings.  Dampers to be mechanically linked together with a leakage rate of not more than 5 CFM/SF at 1 In. W.G. in accordance with ASHRAE 90.1.

Should an external face and bypass damper section be provided, the manufacturer shall provide openings in the casing for the installation of the face and bypass ductwork.

LOUVERS (EXTERIOR WALL)

Refer to Section 10200 - Louvers and Vents.

DAMPER ACTUATORS

Refer to Section 15810 - Ducts or Section 15816 - Non-Metal Ducts.

CONTROLS

Provide temperature/humidity controls consisting of the following:

Microprocessor based return air temperature controller with return air transmitter.

Field installed supply air sensor, discharge air reset sensor and a duct mounted humidistat.

EQUIPMENT CONDENSATE DRAIN PIPING

Refer to Section 15183 - Hydronic Piping.

EXECUTION

INSTALLATION

Install air handling unit under provisions of the manufacturer's instructions.

Mechanical rooms shall be of sufficient size to provide the HVAC equipment     manufacturer's recommended clearances for maintenance and servicing.  A MINIMUM OF THREE FEET CLEARANCE SHALL BE PROVIDED ON BOTH SIDES AND FRONT OF THE AHU AND TWO FEET CLEARANCE IN THE REAR.

Coordinate with the structural engineer and install the AHUs on 6 inch concrete housekeeping pads in the mechanical rooms.  The pads shall extend a maximum of 4 inches beyond the footprint of the supported equipment in all directions and have 1/2 inch chamfered edges.

When the AHUs are provided with a minimum 6 inch factory installed base rails, the use of the 6 inch concrete pads shall not be required.

All AHUs shall be installed on a 3/8” cross-ribbed, oil-resistant, resilient neoprene mounting pad between the unit and the concrete pad or base rail.

Route AHU copper condensate pipe to discharge into the mechanical room floor drain or safewaste (via a 2” minimum air gap) that is connected to the floor drain and routed into the sanitary system.  Floor drain shall be installed immediately adjacent to the 6 inch housekeeping concrete pad.  Should connection to the sanitary system not be possible, provide a floor drain with a backwater valve and connect the condensate into the site storm drain system catch basin only after approval by the SBBC Facilities Design & Support Section.  Floor drains installed in front of the AHU where they can become a tripping hazard are PROHIBITED.

Install spring type vibration isolators between the AHU and the 6 inch concrete housekeeping pad if the AHU fan is not provided with internal spring isolation.  Otherwise, install the AHU on a 3/8 inch cross-ribbed neoprene mounting pads.

Provide 6 inch long flexible duct connectors at all duct connections to rotating or vibrating equipment such as air handler units, unit ventilators, etc.  Refer to Section 15810 - Ducts.

Connect chilled water piping to the AHU so that it is clear of access doors, filters, motor and coil pull area.  It’s preferable that the chilled and condenser water piping be installed behind the unit to allow frontal access and minimize tripping hazards.

During construction, seal the AHU inlet and outlet openings with polyethylene sheet to prevent construction dust and debris from entering AHU.  Verify that during construction, the AHU is fitted with 4 inch depth, MERV 13 efficiency air filters.

Prior to startup, thoroughly clean inside of AHU of all construction dust and debris.

Do not operate AHU until mechanical room has been cleaned and filters are in place.

Provide an analog type differential pressure gauge across the filters to monitor pressure conditions across the filters.

All new AHUs shall be tagged and identified in a sequential numerical format.

Identify AHUs with a minimum 2 inch high stenciled painted, sequential numerical format indicating the building number followed by the equipment number and the area or zone  served such as AHU-1-1/Adminsitration Office, AHU-1-2/Media Center, etc.

TEST AND ADJUST

Start equipment in the presence of the AHU manufacturer’s representative.  Test the unit to demonstrate proper operation at performance requirements specified including running balance, belt slippage, generated noise, proper heating, adequate air flow and unusual or similar indication of improper operation.

Prior to building commissioning (if applicable) and subsequent to test and balance, remove the filters installed during construction and replace with a new set of MERV 13 efficiency air filters.

If sweating occurs on the casing, provide additional foil faced, rigid board insulation of sufficient thickness to be installed on the casing exterior to eliminate the sweating.

Correct any other deficiencies in the AHU operation.

END OF SECTION