# SECTION 15721 (23 77 03)

## OUTSIDE AIR DX PRETREATMENT UNIT WITH HOT GAS REHEAT

- GENERAL

  - SECTION INCLUDES

    - 100 percent outside air DX pretreatment unit (PTU) with hot gas reheat.

  - RELATED SECTIONS

    - Section 15070 - Mechanical Sound and Vibration Control.

    - Section 15083 - Duct Insulation.

    - Section 15810 - Ducts.

    - Section 15816 - Non-Metal Ducts.

    - Section 15825 - Electric Duct Heater.

    - Section 15900 - HVAC and Instrumentation & Controls.

    - Division 16 - Electrical.

  - REFERENCES

    - AMCA 99 - Standards Handbook.

    - AMCA 210 - Laboratory Methods of Testing Fans for Rating Purposes.

    - AMCA 300 - Test Code for Sound Rating Air Moving Devices.

    - ARI 410 - Forced-Circulation Air-Cooling and Air-Heating Coils.

    - ARI 430 - Standard for Central-Station Air-Handling Units.

    - ARI 435 - Standard for Application of Central-Station Air-Handling Units.

    - ANSI/ASHRAE 90.1 - Energy Standard for Buildings Except Low-Rise Residential Buildings.

    - ANSI S12.60-2002 - Acoustical Performance Criteria, Design Requirements & Guidelines for Schools.

    - SMACNA - Low Pressure Duct Construction Standards.

  - QUALITY ASSURANCE

    - Air Coils: Certify capacities, pressure drops and selection procedures in accordance with   ARI 410.

    - Outside Air Pretreatment Unit (PTU): Product of a manufacturer regularly engaged production of components that issues complete catalog data on total product.  The manufacturer of the PTU dehumidification system shall have a minimum of five years experience in the manufacturing of these systems.

    - Design the unit to maximize energy performance.  The minimum mandatory provisions for the HVAC performance are documented in the latest edition of ASHRAE 90.1, Section 6.

    - If the unit is used to cool an interior space without passing through a secondary filtration system, it shall be provided with a filtration media with a Minimum Efficiency Reporting Value (MERV) of 13 with 80-85 percent atmospheric dust spot (ADS).

  - SUBMITTALS

    - Submit shop drawings and manufacturer's installation instructions under provisions of Section 01330 - Submittal Procedures.

    - Shop drawings shall indicate assembly, unit dimensions, weight loading, required clearances, construction details and field connection details.

    - Product data shall indicate dimensions, weights, capacities, ratings, fan performance, acoustical data, motor electrical characteristics, gauges and finishes of materials.

    - Submit electrical requirements for power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring.

  - OPERATION AND MAINTENANCE DATA

    - Submit operation and maintenance data under provisions of Section 01330 - Submittal Procedures.

    - Include instructions for lubrication, filter replacement, motor and drive replacement, spare parts lists and wiring diagrams.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver products to site under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements in factory-fabricated protective containers with factory-installed shipping skids and lifting lugs.

    - Store and protect products under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

    - Store in clean dry place and protect from weather and construction traffic.  Handle carefully to avoid damage to components, enclosures and finish.

  - ENVIRONMENTAL REQUIREMENTS

    - Do not operate units for any purpose, temporary or permanent, until ductwork is clean, filters are in place, bearings lubricated and fan has been test run under observation.

  - EXTRA STOCK

    - Provide one set of 4 inch depth, 80-85 percent atmospheric dust spot (ADS) efficiency, MERV 13 minipleated air filters in accordance with the latest edition of AHSRAE 52.2.

  - WARRANTY

    - Provide manufacturer's one year parts and labor warranty for all the unit’s components and an extended four year parts and labor warranty on the compressor and motor. Both warranties beginning from the date of Beneficial Occupancy.

- PRODUCTS

  - ACCEPTABLE MANUFACTURERS

    - Trane Morganizer OCH

    - Addison

    - Desert Air

    - Lennox

    - Seasons 4

    - District Approved Equal

    - Base Bid Alternate:  The specified base bid manufacturer shall meet the performance and capacities as specified and listed in the unit schedule.

      - In addition, add or deduct alternate may be substituted as indicated in the Bid Form.

      - Alternate shall clearly list any additions, deletions or deviations to the specified equipment.

      - Alternate shall include equipment layout, connections, piping, electrical and control connections.  The unit shall fit in the allocated space as specified.

      - Any additional work and related expenses resulting from the installation of the alternate equipment shall be the responsibility of the installing Contractor.

      - Alternate equipment shall provide full submittals with a line item list of additions, deletions and deviations and approved by the Consulting Engineer ten days prior to the bid date.

  - OUTSIDE AIR PRETREATMENT UNIT (PTU)

    - Factory assembled and pre-wired draw-thru, split system 100 percent outside DX air pretreatment unit with R-410A refrigerant, suitable for constant air volume and consisting of a fan section, compressor(s), dehumidification/cooling coil, hot gas reheat coil, refrigerant receiver, air-cooled condenser, filter section and accessories.

    - Factory test units of sizes, capacities and configuration as indicated and specified.

    - Electrical wiring shall be internal to the unit and be colored and numbered for identification purposes.

    - Base unit performance on sea level conditions.

    - The unit shall be serviceable from two sides as specified.

    - The final equipment location and selection design must comply with the maximum noise criteria levels specified in Section 15070 – Mechanical Sound and Vibration Control, paragraphs 2.3(E) thru (J) for classroom and other core learning spaces.

    - The unit shall achieve a maximum background noise level from heating, ventilating and air conditioning (HVAC) systems in classrooms and other core learning spaces of 45 dBA.  Design classrooms and other core learning spaces to include sufficient sound absorptive finishes for compliance with reverberation time requirements as specified in ANSI Standard S12.60-2002, Acoustical Performance Criteria Design Requirements and Guidelines for Schools.

  - CASING

    - Construct casing and removable panels of 12 gauge, double-wall galvanized steel on channel base.  Casing to be constructed and reinforced to withstand the maximum fan pressures developed.  Fabricate all support pieces of 16 gauge galvanized steel.

    - Units of 4 to15 Tons shall be constructed of 20 gauge outer panels and 22 gauge inner liners.  Units of 20 to 30 Tons shall be constructed of 18 gauge outer panels and 22 gauge inner liners.

    - Insulate casing sections with 1 inch thick rigid foam insulations sandwiched between the outer milled galvanized steel wall and the inner galvanized steel wall.  Minimum insulation R-value of 5.0.

    - Construct drain pan from insulated, 20 gauge double wall stainless steel pitched and positioned under the evaporator end plates to avoid shifting.  It shall be silver solder welded and fitted with a minimum 1 inch male pipe thread (MPT) non-corrosive drain connection and an internal P-trap.

    - The manufacturer shall be responsible for providing additional rigid board type insulation to prevent the air handling unit from sweating under the encountered operating conditions.

  - SUPPLY FAN                                                                                                                               (Units 4 to 15 Tons)

    - Provide fan section with forward curved, double width, double inlet centrifugal type fan.  Air discharge shall be on top of the unit.

    - Blower housing shall be constructed of galvanized steel and mounted on permanently lubricated sealed ball bearings.  The blower housing shall be vibration isolated.

    - Drive pulley and the blower pulley shall be constructed of cast iron. The motor sheave shall be a variable pitch type to allow for field adjustment of the fan CFM.  The drive load service factor shall be a minimum of 1.2.

    - Internally mount fan and motor on a welded steel base coated with zinc chromate. Factory mount motor on slide rails for accessibility.  Provide access to motor, drive and bearings through hinged access doors.

    - Provide motor and fan with internal vibration isolators.

  - SUPPLY FAN                                                                                                                                   (Units 20 to 30 Tons)

    - Provide fan section with a corrosion resistant steel airfoil impeller with backward curved, air foil shaped blades continuously welded in place.  Air discharge shall be on top of the unit.

    - Blower shall be a plenum fan type constructed of heavy gauge welded steel, reinforced with steel stiffeners and painted with an ant-corrosive paint.  The blower housing shall be vibration isolated.

    - Drive pulley and the blower pulley shall be constructed of cast iron. The motor sheave shall be a variable pitch type to allow for field adjustment of the fan CFM.  The drive load service factor shall be a minimum of 1.2.

    - Provide self-aligning, single row, deep groove ball bearings in pillow block cast iron housings.  Grease lubricated ball bearings or ANSI/AFBMA standards, L-50 life at 200,000 hours, pillow block type, self-aligning, grease lubricated roller bearings.  All bearings shall be provided with extended grease lines to the exterior of the unit casing with copper tube and “zerk” fitting rigidly attached to casing to allow lubrication from outside the unit casing.  The operating range of the bearings shall be from –4 Degree F to +176 Degree F.

    - Internally mount fan and motor on a welded steel base coated with zinc chromate. Factory mount motor on slide rails for accessibility.  Provide access to motor, drive and bearings through hinged access doors.

    - Provide motor and fan with internal vibration isolators.

  - MOTORS AND DRIVES

    - Motors: Maximum horsepower as indicated and specified, but not to exceed 20 HP.  Protect motor against contact failure, loss of any phase (single phasing), low voltage, high voltage, voltage unbalance, phase reversal and winding for specified voltage having a minimum power factor of 85 to 100 percent and a minimum efficiency of  91.7 percent at 100 percent load as per IEEE Test Procedure 112, Method B.  Refer to Section 15055 - Motors.

    - Motor shall be TEFC, Class B insulated and designed for continuous operation in 40 Degree C environment and a temperature rise under provisions of ANSI/NEMA MG 1 limits for insulation class, service factor and motor enclosure.

    - Shaft: Solid hot rolled steel, ground and polished with keyway and protectively coated with lubricating oil.

    - V-Belt Drive: Cast iron or steel sheaves, dynamically balanced, bored to fit shaft and keyed. Variable and adjustable pitch sheave selected so that the required RPM is obtained with the sheave set at mid-position; matched belts and drive rated as recommended by the manufacturer or a minimum of 1.2 times the motor rating.

    - Belt Guard: Fabricate to SMACNA Low Pressure Duct Construction Standards of 12 gauge, 3/4 inch diamond mesh wire screen welded to steel angle frame or equivalent and prime coated.  Secure to fan or fan support without short circuiting vibration isolation with provision for adjustment of belt tension, lubrication and use of tachometer with the guard in place.

  - EVAPORATOR DEHUMIDIFICATION COIL

    - Provide coil section with access to both sides of coil.  Enclose coil with headers and return bends fully contained within casing.  Slide coil into unit casing through removable end panels with blank-off sheets and sealing collars at connection penetrations.

    - Provide coil fabricated of seamless drawn copper.  The inner tubing shall be riffled to produce turbulent refrigerant flow in order to enhance the heat transfer process.  The  tubes shall be hydraulically expanded onto the fins to form a permanent metal-to-metal bond for maximum heat transfer.

    - Provide fins which shall be die-formed, lanced aluminum and shall be damage resistant.

    - The evaporator coil shall be positioned to have a space between the evaporator and condenser reheat coil to prevent moisture carryover and re-evaporation.

    - Provide drain pan and downspouts for cooling coil banks of more than one coil high.

    - Ensure face velocity does not exceed 500 FPM.

    - Coil to contain a minimum of six rows and a maximum of 8 to 12 Fins per Inch (FPI).

    - Coil to be pressure tested to 420 PSIG of nitrogen.

  - CONDENSER REHEAT COIL

    - Provide coil section with access to both sides of coil.  Enclose coil with headers and return bends fully contained within casing.  Slide coil into unit casing through removable end panels with blank-off sheets and sealing collars at connection penetrations.

    - Provide coil fabricated of seamless drawn copper.  The inner tubing shall be rifled to produce turbulent refrigerant flow in order to enhance the heat transfer process.  The  tubes shall be hydraulically expanded onto the fins to form a permanent metal-to-metal bond for maximum heat transfer.

    - Provide fins which shall be die-formed, lanced aluminum and shall be damage resistant.

    - The condenser reheat coil shall be positioned to have a space upstream of the evaporator to prevent moisture carryover and re-evaporation.

    - Provide drain pan and downspouts for cooling coil banks of more than one coil high.

    - Ensure face velocity does not exceed 500 FPM.

    - Coil to contain a minimum of six rows and a maximum of 8 to 12 Fins per Inch (FPI).

    - Coil to be pressure tested to 420 PSIG of nitrogen.

  - COMPRESSOR

    - Unit to be a heavy duty, statically and dynamically balanced scroll type compressor with high and low pressure safety switches, internal overheat protection, external vibration isolators and service ports.  On tandem compressors, a factory mounted sensor shall deactivate one compressor when the load reaches midrange.

    - Refrigerant circuit to be equipped with hot-gas bypass on each system compressor which is to be used only for the prevention of coil freezeup and not for compressor unloading.

  - REFRIGERANT

    - Refrigerant shall be R-410A or a refrigerant that does not use CFCs or cause the base building to exceed the threshold set by the formula LCGWP+LCODPx106 ≤100 for ozone depletion and global warming potential.

    - Receiver shall be designed to provide the refrigerant circuit with the proper amount  of refrigerant so that the unit shall operate at the highest efficiency over the entire range of load conditions.

  - RECEIVER

    - Receiver shall be designed to provide the refrigerant circuit with the proper amount of refrigerant so that the outside air PTU shall operate at the highest efficiency over the entire range of load conditions.

  - MIXING BOX

    - Provide mixing box with two position, 24 Volt (power open/spring closed) factory mounted, low leakage type motorized dampers to mix outside air makeup with space return air.

    - Dampers shall be of the air-foiled type with metal compressible jamb seals, extruded vinyl blade edge seals and stainless steel sleeve bearings.  Dampers to be mechanically linked together with a leakage rate of not more than 5 CFM/SQ. FT. at 1 In. W.G.

    - Provide factory mounted temperature and humidity sensors which are to be converted to a dew point value in the microprocessor control and activate the compressor(s) when the dew point rises above 55 Degree F.

    - Provide unit with a factory set Leaving Air Temperature (LAT) which shall be field adjustable at 75 Degree F.

    - Provide unit with a room reset with unoccupied temperature and humidity control.

  - REMOTE AIR-COOLED CONDENSER

    - Provide a full size remote air-cooled condenser in accordance with the plans.  The system shall be capable of rejecting all of the recovered space heat.

    - Construct casing of heavy gauge galvanized steel on channel base.

    - Provide coil fabricated of seamless drawn copper tubing in a staggered design.  The  tubes shall be mechanically expanded onto the full-collared plate type aluminum fins.

    - Fan motors shall be heavy duty PSC or three phase with permanently lubricated ball bearings and built with overload protection.

    - Condenser shall contain dynamically balanced fans with aluminum blades with painted steel hubs and not exceed 30 inches in diameter

    - Fans shall be cycled based on internal head pressure on the multiple fan units and shall be provided with heavy duty fan guards.

    - Coil to contain a minimum of six rows and a maximum of 8 to 12 Fins per Inch (FPI).

    - Coil to be pressure tested to 420 PSIG of nitrogen.

    - Coil to be coated as outlined in Paragraph 2.13.

  - COIL COATING

    - Provide the coil tubing, fins and end plates with a factory applied spray-processed coating for corrosion protection.

    - Ensure coating materials have passed a MINIMUM OF 1000 HOURS OF SALT SPRAY EXPOSURE in testing performed by an independent laboratory under provisions of ASTM B117.85 standards.

    - Ensure the coating material and process as applied to fin tube coils provides an effective corrosion protection in a pH range of 1.0 to 14.0.

    - Prepare the coils through the manufacturer’s procedural cleaning steps allowing for drying prior to the coating process.

    - Apply a  0.5 to 1.0 dry mil thickness of acrylic polymer resin primer.  Coating to be fully cured prior to applying the protective finish coat.

    - Apply the coil corrosion protection coating built-up to a dry mil thickness of 2.0 to 3.0.

    - Ensure the corrosion protection coating is built-up on the fin edges.

    - Ensure the coating is field-repairable and provide touchup product for this purpose.

    - Ensure the company providing the coating process also provides a five year coil warranty.

    - Ensure the entire coating process is similar to the Husky Coil Coat patented process as manufactured by Bronz-Glow Technologies, Inc. (Jacksonville, FL).  Other approved coatings are as manufactured by Thermoguard (Coconut Creek, FL) or Heresite (Manotowac, WI).

  - FILTER SECTION

    - Provide flat type filter section constructed of galvanized steel and containing filter guides and hinged access doors on both sides for side loading of filters.  Provide filter rack capable of accepting 4 inch depth filters.

    - Provide 4 inch depth filter section, UL Class 2, high efficiency, minimum MERV 13 disposable minipleated type air filters with an atmospheric dust spot (ADS) efficiency of 80-85 percent.  Refer to Section 15860 - Air Cleaning Devices.

    - Provide an analog type differential pressure gauge across the filter to monitor dirty filter conditions.

  - EQUIPMENT CONDENSATE DRAIN PIPING

    - Refer to Section 15183 - Hydronic Piping.

  - ROOF CURB                                                                                                                                          (Rooftop Unit)

    - Roof Curb:  Pre-fabricated roof curb fabricated of minimum 18  gauge galvanized steel with continuously welded seams, 2 inch flashing flange, 4 inch minimum deck flange, 1 inch insulation for full height of curb and around inside perimeter of curb.  Roof curb shall be a minimum of 2 inches smaller than the fan to allow for the roof flashing membrane.  Roof curb shall possess a Miami-Dade NOA and be Model GPI as manufactured by Greenheck, Thybar or approved equal.

    - For new construction only, the roof curb height shall be 18 inches above finished roofing with reinforced fastening return at top.

- EXECUTION

  - INSTALLATION

    - Install PTU under provisions of the manufacturer's instructions.

    - Identify each PTU with its tag showing the building number, unit number and area served.  For example, the Locker Room unit shall be labeled “PTU-1-1/Locker Room”.

    - Examine supports receiving the PTU and related ductwork for a level horizontal mounting surface, water tightness, proper anchoring, unevenness, irregularities and incorrect dimensions that would affect the quality and execution of the installation.

    - Mechanical rooms shall be of sufficient size to provide the HVAC equipment manufacturer's recommended clearances for maintenance and servicing.  A MINIMUM OF THREE FEET CLEARANCE SHALL BE PROVIDED ON BOTH SIDES AND FRONT OF THE PTU TWO FEET CLEARANCE IN THE REAR.

    - Coordinate with the structural engineer and install the PTUs on 6 inch concrete housekeeping pads in the mechanical rooms whenever possible.  The pad shall extend a maximum of 4 inches beyond the footprint of the supported equipment in all directions and have 1/2 inch chamfered edges.

    - When installation in mechanical rooms is not possible, the PTUs shall be installed on grade in the building exterior.  In such designs, provide the PTU with a minimum 6 inch factory installed rails so that it can be installed atop a concrete pad.  Rooftop installation shall always be the last design option.

    - Route each PTU copper condensate pipe to discharge into the mechanical room floor drain or safewaste (via a 2” minimum air gap) that is connected to the floor drain and routed into the sanitary system.  Floor drain shall be installed immediately adjacent to the 6 inch housekeeping concrete pad.  Should connection to the sanitary system not be possible, provide a floor drain with a backwater valve and connect the condensate into the site storm drain system catch basin only after approval by the SBBC Design Services Department.  Floor drains installed in front of the PTU where they can become a tripping hazard are PROHIBITED.

    - If the PTU fan is not provided with internal spring isolation, install spring type vibration isolators between the PTU and the 6 inch concrete housekeeping pad.  Otherwise, install the PTU on a 3/8 inch cross-ribbed neoprene mounting pads.

    - Provide 6 inch long flexible duct connectors at all duct connections to rotating or vibrating equipment such as outside air pretreatment units, etc.  Refer to Section 15810 - Ducts.

    - When the installation of rooftop PTUs or piping is unavoidable, permission and a waiver shall be requested from the SBBC Design Services Department.  Upon approval, a minimum 18 inch roof curb or a clearance of 18 inches under the equipment (if no curb is furnished) or piping shall be provided for roof maintenance.

    - Roof mounted equipment shall be anchored to sustain hurricane force winds as outlined in the current ASCE 7 and details of the method of anchoring shall be provided on the mechanical drawings and detailed on the structural drawings.

    - During construction, seal the PTU inlet and outlet openings with polyethylene sheet to prevent construction dust and debris from entering the PTU.  Verify that during construction, the PTU is fitted with 4 inch depth, MERV 13 efficiency air filters.

    - Provide an analog type differential pressure gauge across the filters to monitor pressure conditions across the filters.

    - Prior to startup, thoroughly clean inside of PTU of all construction dust and debris.

    - Do not operate PTU until mechanical room has been cleaned and filters are in place.

  - TEST AND ADJUST

    - Start equipment in the presence of the PTU manufacturer’s representative.  Test the unit to demonstrate proper operation at performance requirements specified including running balance, belt slippage, generated noise, adequate air flow and unusual or similar indication of improper operation.

    - Prior to building commissioning (if applicable) and subsequent to test and balance, remove the filters installed during construction and replace with a new set of MERV 13 efficiency air filters.

    - If sweating occurs on the casing, provide additional foil faced, rigid board insulation of sufficient thickness to be installed on the casing exterior to eliminate the sweating.

    - Correct any other deficiencies in the PTU operation.

END OF SECTION