# SECTION 15724 (23 77 01)

## PACKAGED DX AIR CONDITIONING UNIT                                                    WITH HOT GAS REHEAT

- GENERAL

  - SECTION INCLUDES

    - Packaged air conditioning DX air handling unit with hot gas reheat.

  - RELATED SECTIONS

    - Section 15055 - Motors.

    - Section 15070 - Mechanical Sound and Vibration Control.

    - Section 15083 - Duct Insulation.

    - Section 15810 - Metal Ducts.

    - Section 15816 - Non-Metal Ducts.

    - Section 15825 - Electric Duct Heater.

    - Section 15900 - HVAC Instrumentation & Controls.

    - Division 16 - Electrical.

  - REFERENCES

    - AMCA 99 - Standards Handbook.

    - AMCA 210 - Laboratory Methods of Testing Fans for Rating Purposes.

    - AMCA 300 - Test Code for Sound Rating Air Moving Devices.

    - ARI 410 - Forced-Circulation Air-Cooling and Air-Heating Coils.

    - ARI 430 - Standard for Central-Station Air-Handling Units.

    - ARI 435 - Standard for Application of Central-Station Air-Handling Units.

    - ANSI/ASHRAE 90A - Energy Conservation in New Building Design.

    - ANSI S12.60 - Acoustical Performance Criteria, Design Requirements & Guidelines for     Schools.

    - SMACNA - Low Pressure Duct Construction Standards.

  - QUALITY ASSURANCE

    - Air Coils: Certify capacities, pressure drops and selection procedures in accordance with ARI 410.

    - Air Conditioning Unit: Product of a manufacturer regularly engaged in production of components that issues complete catalog data on total product.  All 	equipment shall meet SBBC standards including noise criteria.

  - SUBMITTALS

    - Submit shop drawings and manufacturer's installation instructions under provisions of Section 01330 - Submittal Procedures.

    - Shop drawings shall indicate assembly, unit dimensions, weight loading, required clearances, construction details and field connection details.

    - Product data shall indicate dimensions, weights, capacities, ratings, fan performance, acoustical data, motor electrical characteristics, gauges and finishes of materials.

    - Submit electrical requirements for power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring.

  - OPERATION AND MAINTENANCE DATA

    - Submit operation and maintenance data under provisions of Section 01330 - Submittal Procedures.

    - Include instructions for lubrication, filter replacement, motor and drive replacement, spare parts lists and wiring diagrams.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver products to site under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements in factory-fabricated protective containers with factory-installed shipping skids and lifting lugs.

    - Store and protect products under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

    - Store in clean dry place and protect from weather and construction traffic.  Handle carefully to avoid damage to components, enclosures and finish.

  - ENVIRONMENTAL REQUIREMENTS

    - Do not operate units for any purpose, temporary or permanent, until ductwork is clean, filters are in place, bearings lubricated and fan has been test run under observation.

  - EXTRA STOCK

    - Provide one set of 4 inch depth, 80-85 percent atmospheric dust spot (ADS) efficiency, MERV 13 minipleated filters in accordance with the latest edition of ASHRAE 52.2.

- PRODUCTS

  - ACCEPTABLE MANUFACTURERS

    - Trane

    - Carrier

    - York

    - McQuay

  - AIR HANDLING UNIT

    - Factory assembled and pre-wired draw-thru type air handling unit with R-410A refrigerant, suitable for constant air volume operation and consisting of a fan section, compressor(s), evaporator, hot gas reheat coil, refrigerant receiver, air-cooled condenser, face and bypass section, filter section and accessories.

    - Factory tested air handling units of sizes, capacities and configuration as indicated and specified.

    - Base air handling unit performance on sea level conditions.

    - The unit shall be serviceable from two sides as specified.

    - The final equipment location and selection design must comply with the maximum noise criteria levels specified in Section 15070 – Mechanical Sound and Vibration Control, paragraphs 2.3(E) thru (J) for classroom and other core learning spaces.

    - The unit shall achieve a maximum background noise level from heating, ventilating and air conditioning (HVAC) systems in classrooms and other core learning spaces of 45 dBA.  Design classrooms and other core learning spaces to include sufficient sound absorptive finishes for compliance with reverberation time requirements as specified in ANSI Standard S12.60-2002, Acoustical Performance Criteria Design Requirements and Guidelines for Schools.

  - CASING

    - Construct casing of 16 gauge, double-wall galvanized steel on channel base.  Casing to be constructed and reinforced to withstand the maximum fan pressures developed.  Fabricate channel base of galvanized welded steel.

    - Casing shall include insulated, hinged, double wall access doors in the filter, fan and coil sections.

    - Insulate casing sections with 1 inch thick/3 PCF density or 2 inch thick/1.5 PCF uncompressed insulation sandwiched between the outer milled galvanized steel wall and the inner galvanized steel wall.  Minimum insulation R-value of 4.2.

    - Construct drain pan from insulated, double wall stainless steel with welded corners and a bottom drain. Pitch entire pan to drain connection.

    - The manufacturer shall be responsible for providing additional rigid board type insulation to prevent the air handling unit from sweating under the encountered operating conditions.

  - SUPPLY FAN

    - Provide fan section with forward curved, double width, double inlet (DWDI) centrifugal type fan.

    - Provide self-aligning, grease lubricated ball or roller bearings with lubrication fittings extended to exterior of fan casing with copper tube and “zerk” fitting rigidly attached to casing.

    - Internally mount fan and motor on a welded steel base coated with zinc chromate. Factory mount motor on slide rails for accessibility.  Provide access to motor, drive and bearings through hinged access doors.

    - Provide motor and fan with internal vibration isolators.

  - MOTORS AND DRIVES

    - Motors: Maximum horsepower as indicated and specified, but not to exceed 20 HP.  Protect motor against contact failure, loss of any phase (single phasing), low voltage, high voltage, voltage unbalance, phase reversal and winding for specified voltage having a minimum power factor of 85 to 100 percent and a minimum efficiency of 91.7 percent at 100 percent load as per IEEE Test Procedure 112, Method B.  Refer to Section 15055 - Motors.

    - Design for continuous operation in 40 Degree C environment and for temperature rise under provisions of ANSI/NEMA MG 1 limits for insulation class, service factor and motor enclosure.

    - Bearings: ANSI/AFBMA 9, L-50 life at 100,000 hours, heavy duty pillow block type, self-aligning, Grease lubricated ball bearings or ANSI/AFBMA 11, L-10 life at 120,000 hours, pillow block type, self-aligning, grease lubricated roller bearings.  All bearings shall be provided with extended grease lines to allow lubrication from outside the AHU casing.

    - Shaft: Solid hot rolled steel, ground and polished with keyway and protectively coated with lubricating oil.

    - V-Belt Drive: Cast iron or steel sheaves, dynamically balanced, bored to fit shaft and keyed. Variable and adjustable pitch sheave for motors 15 HP and under selected so that the required RPM is obtained with the sheave set at mid-position; fixed sheave for 20 HP and larger, matched belts and drive rated as recommended by the manufacturer or a minimum of 1.5 times the motor rating.

    - Belt Guard: Fabricate to SMACNA Low Pressure Duct Construction Standards of 12 gauge, 3/4 inch diamond mesh wire screen welded to steel angle frame or equivalent and prime coated.  Secure to fan or fan support without short circuiting vibration isolation with provision for adjustment of belt tension, lubrication and use of tachometer with the guard in place.

  - EVAPORATOR COIL, OUTSIDE AIR PRE-COOLING COIL & HOT GAS REHEAT COIL

    - Provide coil section with access to both sides of coil.  Enclose coil with headers and return bends fully contained within casing.  Slide coil into air handling unit casing through removable end panels with blank-off sheets and sealing collars at connection penetrations.

    - Provide drain pan and downspouts for cooling coil banks of more than one coil high. Coils to be of sufficient free area and not incorporate moisture eliminators or coatings to prevent water carryover.

    - Provide coils indicated for DX cooling. Ensure face velocity does not exceed 500 FPM.

    - Construct coils of 1/2 inch minimum copper tubes mechanically expanded into aluminum fins.

    - Coil to contain a minimum of six rows and a maximum of 8 to 12 Fins per Inch (FPI).  All refrigerant evaporators shall be furnished with an externally equalized, thermostatic expansion valve, factory supplied, mounted and piped.   The field connections shall be made to the suction and liquid line connections furnished by the manufacturer at the side of the unit.  The sensing bulb for the expansion valve shall be field installed on the suction line immediately outside of the handler casing.

    - The unit shall contain a hot gas reheat coil with a modulating reheat control valve and an electronic controller.  The valve position shall be controlled to provide a specific supply air temperature setpoint that is set on the control board or sent to the control board by a remote 0-10 Volt DC signal to control the space and relative humidity in the occupied space.  The hot gas reheat coil shall be provided with a modulating face and bypass reheat control.

  - REFRIGERANT

    - Refrigerant shall be R-410A or a refrigerant that does not use CFCs or cause the base building to exceed the threshold set by the formula LCGWP+LCODPx106 ≤100 for ozone depletion and global warming potential.

    - Receiver shall be designed to provide the refrigerant circuit with the proper amount  of refrigerant so that the outside air pretreatment unit shall operate at the highest efficiency over the entire range of load conditions.

  - PRESSURE INDEPENDENT CHARACTERIZED CONTROL VALVE (PICCV)

    - Refer to Section 15900 - HVAC instrumentation and Controls.

  - COIL COATING

    - Provide the coil tubing, fins and end plates with a factory applied spray-processed coating for corrosion protection.

    - Ensure coating materials have passed a MINIMUM OF 1000 HOURS OF SALT SPRAY EXPOSURE in testing performed by an independent laboratory under provisions of ASTM B117.85 standards.

    - Ensure the coating material and process as applied to fin tube coils provides an effective corrosion protection in a pH range of 1.0 to 14.0.

    - Prepare the coils through the manufacturer’s procedural cleaning steps allowing for drying prior to the coating process.

    - Apply a  0.5 to 1.0 dry mil thickness of acrylic polymer resin primer.  Coating to be fully cured prior to applying the protective finish coat.

    - Apply the coil corrosion protection coating built-up to a dry mil thickness of 2.0 to 3.0.

    - Ensure the corrosion protection coating is built-up on the fin edges.

    - Ensure the coating is field-repairable and provide touchup product for this purpose.

    - Ensure the company providing the coating process also provides a five year coil warranty.

    - Ensure the entire coating process is similar to the Husky Coil Coat patented process as manufactured by Bronz-Glow Technologies, Inc. (Jacksonville, FL).  Other approved coatings are as manufactured by Thermoguard (Coconut Creek, FL) or Heresite (Manotowac, WI).

  - FACE AND BYPASS SECTION                                                                                     (Constant Volume Systems Only)

    - Provide factory mounted face and bypass dampers of the air-foiled, opposed galvanized steel blade type with metal compressible jamb seals, extruded vinyl blade edge seals and stainless steel sleeve bearings.  Dampers to be mechanically linked together with a leakage rate of not more than 5 CFM/SQ. FT. at 1 In. W.G.

    - Should an external face and bypass damper section be provided, the manufacturer shall provide openings in the casing for the installation of the face and bypass ductwork.

  - FILTER SECTION

    - Provide flat type filter section constructed of galvanized steel and containing filter guides and hinged access doors on both sides for side loading of filters.  Provide filter rack capable of accepting 4 inch depth filters.

    - Provide 4 inch depth filter section, UL Class 2, high efficiency, minimum MERV 13 disposable minipleated type air filters with an atmospheric dust spot (ADS) efficiency of 80-85 percent.  Refer to Section 15860 - Air Cleaning Devices.

    - Provide an analog differential pressure gauge across the filter to monitor dirty filter conditions.

  - DAMPER ACTUATORS

    - Refer to Section 15810 - Ducts or Section 15816 - Non-Metal Ducts.

  - CONTROLS

    - Provide temperature/humidity controls consisting of the following:

      - Microprocessor based return air temperature controller with return air transmitter.

      - Field installed supply air sensor, discharge air reset sensor and a duct mounted humidistat.

  - EQUIPMENT CONDENSATE DRAIN PIPING

- Refer to Section 15183 - Hydronic Piping.

- EXECUTION

  - INSTALLATION

    - Install air handling unit under provisions of the manufacturer's instructions.

    - Identify each air handling unit with its tag showing the building number, unit number and area served.  For example, the Media Center unit shall be labeled “AHU-1-1/Media Center”.

    - Mechanical rooms shall be of sufficient size to provide the HVAC equipment manufacturer's recommended clearances for maintenance and servicing.  A MINIMUM OF THREE FEET CLEARANCE SHALL BE PROVIDED ON BOTH SIDES AND FRONT OF THE AHU AND TWO FEET CLEARANCE IN THE REAR.

    - Coordinate with the structural engineer and install the AHU on a 6 inch concrete housekeeping pad in the mechanical room.  The pad shall extend a maximum of 4 inches beyond the footprint of the supported equipment in all directions and have 1/2 inch chamfered edges.

    - When the AHUs are provided with a minimum 6 inch factory installed rails, the use of the 6 inch concrete pads shall not be required.

    - All AHUs shall be installed on a 3/8” cross-ribbed, oil-resistant, resilient neoprene mounting pad between the unit and the concrete pad or rail.

    - Route each AHU copper condensate pipe to discharge into the mechanical room floor drain or safewaste (via a 2” minimum air gap) that is connected to the floor drain and routed into the sanitary system.  Floor drain shall be installed immediately adjacent to the 6 inch housekeeping concrete pad.  Should connection to the sanitary system not be possible, provide a floor drain with a backwater valve and connect the condensate into the site storm drain system catch basin only after approval by the SBBC Facilities Design & Support Section.  Floor drains installed in front of the AHU where they can become a tripping hazard are PROHIBITED.

    - Install spring type vibration isolators between the AHU and the 6 inch concrete housekeeping pad if the AHU fan is not provided with internal spring isolation.  Otherwise, install the AHU on a 3/8 inch cross-ribbed neoprene mounting pads.

    - Provide 6 inch long flexible duct connectors at all duct connections to rotating or vibrating equipment such as air handler units, unit ventilators, etc.  Refer to Section 15810 - Ducts.

    - Connect refrigerant piping to the AHU so that it is clear of access doors, filters, motor and coil pull area.  It’s preferable that the refrigerant piping be installed behind the unit to allow frontal access and minimize tripping hazards.

    - During construction, seal the AHU inlet and outlet openings with polyethylene sheet to prevent construction dust and debris from entering AHU.  Verify that during construction, the AHU is fitted with 4 inch depth, MERV 13 efficiency air filters.

    - Prior to startup, thoroughly clean inside of AHU of all construction dust and debris.

    - Do not operate AHU until mechanical room has been cleaned and filters are in place.

    - Provide an analog type differential pressure gauge across the filters to monitor pressure conditions across the filters.

  - TEST AND ADJUST

    - Start equipment in the presence of the AHU manufacturer’s representative.  Test the unit to demonstrate proper operation at performance requirements specified including running balance, belt slippage, generated noise, proper heating, adequate air flow and unusual or similar indication of improper operation.

    - Prior to building commissioning (if applicable) and subsequent to test and balance, remove the filters installed during construction and replace with a new set of MERV 13 efficiency air filters.

    - If sweating occurs on the casing, provide additional foil faced, rigid board insulation of sufficient thickness to be installed on the casing exterior to eliminate the sweating.

    - Correct any other deficiencies in the AHU operation.

END OF SECTION