# SECTION 15734 (23 74 06)                                                                       PACKAGED EHPA ROOFTOP DX AIR CONDITIONING UNIT  WITH HOT GAS REHEAT

- GENERAL

  - SECTION INCLUDES

    - Packaged rooftop DX air conditioning unit with hot gas reheat designed for use in designated EHPA Special Needs Area only.

    - Unit controls.

    - Remote panel.

    - Roof mounting curb and base.

  - RELATED SECTIONS

    - Section 15055 - Motors.

    - Section 15060 - Hangers and Supports.

    - Section 15070 - Mechanical Sound and Vibration Control.

    - Section 15083 - Duct Insulation.

    - Section 15900 - HVAC Instrumentation and Controls.

    - Division 16 - Electrical

  - REFERENCES

    - ANSI/ASHRAE 90A - Energy Conservation in New Building Design.

    - ANSI S12.60-2002 - Acoustical Performance Criteria, Design Requirements and Guidelines for Schools.

    - ARI 210 - Unitary Air Conditioning Equipment.

    - ARI 270 - Sound Rating of Outdoor Unitary Equipment.

    - NFPA 70 - National Electric Code.

  - SUBMITTALS

    - Submit product data under provisions of Section 01330 - Submittal Procedures.

    - Submit manufacturer's installation instructions under provisions of Section 01330 - Submittal Procedures.

    - Product data shall indicate dimensions, weights, capacities, ratings, fan performance acoustical data, motor electrical characteristics, gauges and finishes of materials.

    - Submit electrical requirements for power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring.

  - OPERATION AND MAINTENANCE DATA

    - Submit operation and maintenance data.

    - Include manufacturer's descriptive literature, operating instructions, installation instructions, maintenance and repair data and parts listing.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver products to site under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

    - Store and protect products under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

    - Protect unit from physical damage by storing off site until mounting frames are in place, ready for immediate installation of unit.

  - WARRANTY

    - Provide manufacturer's one year parts and labor warranty for all the A/C unit’s components and an extended four year parts and labor warranty on the compressor and motor. Both warranties beginning from the date of Beneficial Occupancy.

- PRODUCTS

  - ACCEPTABLE MANUFACTURERS

    - Trane

    - Carrier

    - York

    - Lennox

    - McQuay

    - Reznor

    - Seasons 4

  - AIR CONDITIONING UNIT

    - Self-contained, packaged roof mounted, air-to-air DX air conditioning unit having the capability of cooling the required capacity of outside air from 91 Degree Fdb/78 Degree Fwb so as to supply room air at 75 Degree Fdb/50 percent RH.

    - Heating is not required for the unit installed in the EHPA since this unit shall be operable only during hurricane periods.

    - Unit to be a high efficiency, factory assembled, pre-wired, draw-thru unit with a minimum of 13 SEER, R-410A refrigerant, suitable for low pressure operation and consist of a cabinet and frame, supply fan, controls, air filters, vertical discharge ducting, roof curb, serviceable access panels with screwdriver operated flush cam type fasteners, refrigerant cooling coil and compressor, condenser coil and fan and compressor reheat recovery controlled by a duct mounted humidistat.

    - Provide unit with a premium quality motorized outside air damper and a manual volume damper for fixed outside air makeup quantity.

    - The final equipment location and design selection design shall comply with the maximum noise criteria levels specified in paragraph 2.3(E) of Section 15070 – Mechanical Sound and Vibration Control for classrooms and other core learning spaces.

    - The unit shall achieve a maximum background noise level from heating, ventilating and air conditioning (HVAC) systems in classrooms and other core learning spaces of 45 dBA.  Design classrooms and other core learning spaces to include sufficient sound absorptive finishes for compliance with reverberation time requirements as specified in ANSI Standard S12.60-2002, Acoustical Performance Criteria Design Requirements and Guidelines for Schools.

  - CASING

    - Galvanized steel bonderized and coated with baked enamel finish, access doors or removable access panels with quick screwdriver operated flush cam type fasteners.  Structural members to be minimum 18 gauge.  Removable panels to be minimum 20 gauge.  Insulate unit with 1/2 inch thick, 3 PCF density, neoprene coated glass fiber insulation, “k” value of 0.26 at 75 Degree F.  Insulation to be adhered and pinned to the casing.

    - Construct drain pan from galvanized steel with welded corners and a bottom drain.  Pitch entire pan to drain connection.

    - The manufacturer will be responsible for providing additional rigid board type insulation to prevent the unit from sweating under the encountered operating conditions.

  - SUPPLY FAN

    - Forward curved, double width, double inlet centrifugal type fan resiliently mounted with V-belt drive and rubber isolated hinge mounted motor.

  - CONDENSER FAN

    - Direct drive, statically and dynamically balanced propeller fan, permanently lubricated and weatherproof motor UL listed for outdoor use, resiliently mounted with fan guard, motor overload protection, wired to operate with compressor.

  - MOTORS AND DRIVES

    - Motors:  Maximum horsepower as indicated and specified.  Protect motor against contact failure, loss of any phase (single phasing), low voltage, high voltage, voltage unbalance, phase reversal and wind for specified voltage having a minimum power factor of 85 to 100 percent and a minimum efficiency of 91.7 percent at 100 percent load as per IEEE Test Procedure 112, Method B.  Refer to Section 15052 - Variable Frequency Drive or Section 15055 - Motors.

    - Design for continuous operation in 40 Degree C environment and for temperature rise under provisions of ANSI/NEMA MG 1 limits for insulation class, service factor and motor enclosure.

  - EVAPORATOR COIL

    - Evaporator coil with minimum 3/8 inch copper tubes mechanically expanded onto aluminum plate fins.

  - COIL COATING

    - Provide the coil tubing, fins and end plates with a factory applied dip-processed coating for corrosion protection.

    - Ensure coating materials have passed a MINIMUM OF 1000 HOURS OF SALT SPRAY EXPOSURE in testing performed by an independent laboratory under provisions of ASTM B117.97 standards.

    - Ensure the coating material and process as applied to fin tube coils provides an effective corrosion protection in a pH range of 1.0 to 14.0.

    - Prepare the coils through the manufacturer’s procedural cleaning steps allowing for drying prior to the coating process.

    - Apply a 0.5 to 1.0 dry mil thickness of acrylic polymer resin primer.  Coating to be fully cured prior to applying the protective finish coat.

    - Apply the coil corrosion protection coating built-up to a dry mil thickness of 2.0 to 3.0.

    - Ensure the corrosion protection coating is built-up on the fin edges.

    - Ensure the coating is field-repairable and provide touchup product for this purpose.

    - Ensure the entire coating process is similar to the Husky Coil Coat patented process as manufactured by Bronz-Glow Technologies, Inc. (Jacksonville, FL).  Other approved coatings are as manufactured by Thermoguard (Coconut Creek, FL) or Heresite (Manotowac, WI).

    - Ensure the company providing the coating process also provides a five year coil warranty.

  - FILTER SECTION

    - Provide flat type filter section constructed of galvanized steel and containing filter guides and hinged access doors on both sides for side loading of filters.

    - Provide 4 inch depth filter section, UL Class 2, high efficiency, minimum MERV 13 disposable, minipleated type air filters with an atmospheric dust spot (ADS) efficiency of 80-85 percent.  Refer to Section 15860 - Air Cleaning Devices.

  - REFRIGERANT CIRCUIT

    - Unit to contain one sealed refrigerant circuit including one hermetic compressor, thermal expansion valve metering device, finned tube air-to-refrigerant heat exchanger, refrigerant expansion valve and service ports.

    - Compressor to be a high efficiency type designed for cooling only and mounted on vibration isolators. Provide compressor motor with internal overload protection.

    - Finned tube coil to be constructed of lanced aluminum fins not exceeding eleven per inch bonded to rifled copper tubes in a staggered pattern not less than six row deep and have a 450 PSIG working pressure.

    - Refrigerant circuit to be equipped with hot-gas reheat for control of the relative humidity of the supply air.

  - REFRIGERANT

    - Refrigerant: Chiller refrigerant to be R-410A or a refrigerant that does not use CFCs or cause the project to exceed the threshold set by the formula LCGWP + LCODP X 106  ≤ 100 for ozone depletion and global warming potential.

    - Receiver shall be designed to provide the refrigerant circuit with the proper amount  of refrigerant so that the unit shall operate at the highest efficiency over the entire range of load conditions.

  - ROOF CURB

    - Roof Curb:  Pre-fabricated roof curb fabricated of minimum 18  gauge galvanized steel with continuously welded seams, 2 inch flashing flange, 4 inch minimum deck flange, 1 inch insulation for full height of curb and around inside perimeter of curb.  Roof curb shall be a minimum of 2 inches smaller than the fan to allow for the roof flashing membrane.  Roof curb shall possess a Miami-Dade NOA and be Model GPI as manufactured by Greenheck, Thybar or approved equal.

    - Roof curb height shall be 18 inches above finished roofing with reinforced fastening return at top.

  - PIPING

    - Condenser and condensate drain connections to be constructed of brass female pipe thread fittings mounted flush to side of cabinet exterior with optional stainless steel, braided hose kit with swivel connectors.  Condensate piping to be copper Type “L”.

  - ELECTRICAL

    - Factory or field installed energy management relay to allow unit control by an external source.

    - Provide a lockout indicating terminal in the low voltage circuit.

    - When the safety controls are activated to prevent compressor short cycling, the lockout circuit must be reset at the thermostat or main circuit breaker.

    - Disconnect Switch:  Factory mount disconnect switch.

  - CONTROLS

    - Provide temperature/humidity controls consisting of field installed supply air sensor, discharge air reset sensor and duct mounted humidistat.

    - Controls to be a low voltage, electric solid state microcomputer based room thermostat located as indicated. If connection to the Andover Controls Energy management/Security (EM/S) System is not possible, ensure room thermostat incorporates:

      - Preferential rate control to minimize overshoot deviation from set point.

      - Instant override of set point for continuous or timed period from one hour to 31 days.

      - Short cycle protection.

      - Switch selection features including digital display, remote sensor, fan on-auto.

    - Ensure room thermostat display includes:

      - Time of day.

      - Actual room temperature.

      - System Model Indication:  Cooling, auto, off, fan auto, fan on.

  - EQUIPMENT CONDENSATE DRAIN PIPING

    - Refer to Section 15183 - Hydronic Piping.

- EXECUTION

  - INSPECTION

    - Examine supports to receive unit and related ductwork for:

      - Horizontal mounting surface.

      - Water tightness.

      - Proper anchoring.

      - Unevenness, irregularities and incorrect dimensions that would affect quality and execution of installation.

    - Verify that proper power supply is available.

    - Do not proceed with installation until supports conform to specifications requirements.

  - INSTALLATION

    - Install unit under provisions of the manufacturer's instructions.

    - Identify unit with its tag showing the building number, unit number and area served.  For example, label the EHPA unit “AC-1-1/EHPA”.

    - Mount unit on a factory built roof mounting curb providing a watertight enclosure to protect the ductwork and utility services.  Verify that the roof mounting curb is installed level.

    - Unit shall be mounted on a raised support having a minimum height clearance of 18 inches for units having a width of up to 36 inches.  For units having widths greater than 36 inches, clearance heights as outlined in Table 1509.7 of the FBC - Building shall be used.

    - Unit shall be anchored to sustain hurricane force winds as outlined in the current ASCE 7 and details of the method of anchoring shall be provided on the mechanical drawings and detailed on the structural drawings.

    - Verify that during construction, the unit is fitted with 4 inch depth, MERV 13 efficiency air filters.

    - During construction, keep unit inlet and outlet sealed with polyethylene sheet to prevent accumulation of construction dust inside unit.

    - The dedicated roof mounted unit shall be electrically connected to the facility emergency generator so that it is operable during hurricanes and other electrical outage periods.

  - CLEANING

    - Clean tar or other debris from exterior of casings.

    - Remove debris and waste materials resulting from installation.

    - Clean inside of ductwork as called for in Section 15810 - Ducts.

    - Do not operate unit until area served has been cleaned and filters are in place.

  - TEST AND ADJUST

    - Start equipment in presence of the unit manufacturer representative noting any unbalance, slippage of belts, unusual or similar indication of improper operation.

    - After installation, test unit to demonstrate proper operation of unit at performance requirements specified including running balance and noise considerations, proper cooling air flow.

    - Correct any deficiencies in unit operation.

    - Prior to building commissioning and subsequent to test and balance, remove the filters and replace with a new set of MERV 13 efficiency air filters.

END OF SECTION