- SECTION 15788 (23 ?? ??)

- REFRIGERATION SYSTEM SAFETY EQUIPMENT

- GENERAL

  - SECTION INCLUDES

- A.	       Refrigerant monitors for chiller rooms.

  - RELATED SECTIONS

    - Section 15075 - Mechanical Identification.

    - Section 15183 - Hydronic Piping.

    - Section 15620 - Packaged Water Cooled Chiller.

    - Division 15 - Plumbing.

    - Division 16 - Electrical.

  - REFERENCES

    - ASHRAE 15 - Safety Code for Mechanical Refrigeration

    - ANSI/NFPA 1981-1987 Edition, and MSHA certification TC-13F-140.

    - ANSI A13.1 Scheme for Identification of Piping Systems.

  - SUBMITTALS

    - Submit product data under provisions of Section 01330 - Submittal Procedures.

    - Submit manufacturer's shop drawings and installation instructions for approval before ordering or starting work under provisions of Section 01330 - Submittal Procedures.

  - DELIVERY, STORAGE AND HANDLING

    - Protect equipment during storage and installation. Cover equipment with corresponding shipping container or other appropriate material after unit is set in place to protect unit from damage from construction debris or paint and plaster splatter.

- PRODUCTS

  - ACCEPTABLE MANUFACTURERS - REFRIGERANT MONITOR

    - McQuay

    - Trane RMWD

    - Yokogawa USA

    - Brash BBS

  - REFRIGERANT MONITOR

    - Employ infrared photo acoustic sensor technology to provide sensing capability up to one part per million (ppm). Provide the ability to differentiate between compounds of all commonly used refrigerants. Equip the monitor with the following features:

      - Power Supply: 120 VAC, single phase.

      - NEMA-4 Construction.

      - Calibration for R-123, R-134A or R-410A.

      - Provide analog output to connect to analog input of Energy Management/Security System to provide trending information for refrigerant levels in equipment room. Output shall be 0-10 VDC and 4-20 mA. Output shall be adjustable and may be set at 0-100 or 1-100 ppm.

      - Provide auxiliary contacts available for use in initiating the fire alarm system, the security system and visual alarms at mechanical room entrances.

      - Provide a front panel display showing concentration information, alarms and service diagnostics.

      - Provide three levels of concentration alarms and a trouble alarm. The system may be reset at the monitor or may be reset remotely.  Alarms shall be field adjustable and may be configured to be latching or non-latching.

      - Provide field-installed, remote-mounted audible alarm with three level flashing lights (red, yellow and blue).

      - Provide field-installed visual alarms at each mechanical room entrance. Visual alarm shall be rotating beacon with magnifying red lens, 120 VAC, Model 49R-N5 as manufactured by Edwards.

      - Provide sample filters.

      - The monitor pickup points shall be 18 inches above the floor and located as close to the refrigerant source as possible between the refrigerant source and the dedicated room exhaust fan, but not over 50 feet from the refrigerant source. Provide multiple sensors and a multi-channel scanner if necessary to keep the distance from the sensor to the refrigerant source less than 50 feet.

  - OXYGEN MONITOR

    - The monitor shall use a non-depleting coulometric or electrochemical sensor cell.

      - The unit shall have a measurement range of 0-25 percent and an accuracy of plus or minus 1 percent of full scale.

      - Response time shall be a minimum of 90 percent if full reading within 30 seconds.

      - The unit must have at least two adjustable alarm set points each with a binary contact closure for remote indication.

      - An analog corresponding to the display value must be available for remote indication.

      - An analog corresponding to the display value shall be available for remote monitoring with the building management system or other recording equipment.

  - SIGNAGE

    - Each refrigerating system sign erected on the premises shall be easily legible, permanent, securely attached and easily accessible.  Signage shall indicate:

      - Name and address of the installer.

      - Type and initial charge if refrigerant.

      - The field test pressure applied.

    - Systems containing more than 100 Lbs. of refrigerant shall be provided with durable signs having not less than 0.5 inch in height and designating:

      - Valves or switches for controlling the refrigerant flow, the ventilation and the refrigerant compressors.

      - The type of refrigerant or secondary coolant contained in the exposed piping outside the machinery room, if applicable. Piping identification shall be according to ANSI A13.1, Scheme for Identification of Piping Systems. Legends indicating flow direction, function, temperature or pressure may also be used according to accepted practice.

    - Post emergency shutdown procedure, including precautions to be observed in case of a breakdown or leak, shall be installed outside of the machinery room immediately next to each door. These precautions shall address:

      - Instructions for shutting down the system in case of emergency.

      - Name, address, day/night telephone numbers to notify the department having jurisdiction and instructions in case of emergency.

    - Signage shall comply with Section 15075 of these specifications.

- EXECUTION

  - INSTALLATION

    - Install equipment according to plans and applicable manufacturer's instructions.

- END OF SECTION