# SECTION 15816 (23 31 16)

## NONMETAL DUCTS

- GENERAL

  - SECTION INCLUDES

    - Low pressure phenolic foam pre-insulated duct.

    - Fire and smoke dampers.

  - RELATED SECTIONS

    - Section 15060 - Hangers and Supports.

    - Section 15825 - Electric Duct Heater.

    - Section 15850 - Air Outlets and Inlets.

  - REFERENCES

    - ASHRAE - Fundamentals Handbook; Chapter 32 - Duct Design, Latest Edition.

    - ASHRAE - HVAC Systems and Equipment; Chapter 16 - Duct Construction, Latest Edition.

    - SMACNA Leakage, Class 6.

    - UL 181 - Air Duct Standards.

    - UL 555 - Fire Dampers.

    - UL555S - Smoke Dampers.

  - DEFINITIONS

    - Pressure Classifications:

      - Low Pressure/Low Velocity:  Less than or equal to 2 inch water gauge (WG) positive or negative static pressure and velocities less than 2,500 FPM.

    - Duct Sizes:  Inside clear dimensions are indicated on drawings.  For double wall insulated duct, free inside clear dimensions shall be maintained.

    - Low Pressure:

      - Three Pressure Classifications:

        - 1/2 inch WG positive or negative static pressure and velocities less than 2,000 fpm.

        - 1 inch WG positive or negative static pressure and velocities less than 2,500 fpm.

        - 2 inch WG positive or negative static pressure and velocities less than 2,500 fpm.

    - Ductwork:

      - Duct Pressure Classification:  As required for the pressure available from the fan or a minimum of 2 inch WG, whichever is greater.

      - Ductwork to be sealed to SMACNA Class 6 leakage requirements including the transverse joints, fitting connections, 45 degree takeoff connections, bellmouth connections and longitudinal seams.

      - Duct material not to exceed 25 Flame Spread and 50 Smoke Developed.

  - REGULATORY REQUIREMENTS

    - Construct ductwork to ANSI/NFPA 90A and 96 standards.

  - SUBMITTALS

    - Submit detailed ductwork coordination plans drawn to a scale of not less than 1/4 inch = 1’-0” for general building areas and 3/8 inch = 1’-0” for mechanical rooms and similar congested areas under provisions of Section 01330 - Submittal Procedures.  Provide elevation views of equipment such as air handling units, fans, hoods, etc.

    - Shop Drawings: Submit detailed ductwork coordination plans drawn to a scale of not less than 1/4 inch = 1’-0” for general building areas, mechanical rooms and similar congested areas.  Indicate duct routing, duct dimensions, elevation of ducts above finished floor, duct fittings, standard shop practices and particulars such as gauges, sizes welds and configuration prior to start of work.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver products to site under provisions of Section 01663 Product Delivery, Storage and Handling Requirements.

    - Store and protect products under provisions of Section 01663 - Product Delivery, Storage and Handling Requirements.

- PRODUCTS

  - ACCEPTABLE MANUFACTURERS - DUCTWORK

    - Kingspan Koolduct

    - No Substitutes

  - ACCEPTABLE MANUFACTURERS - FLEXIBLE DUCT

    - Omniaire

    - Atco

    - Thermaflex

  - ACCEPTABLE MANUFACTURERS - FIRE DAMPERS

    - Nailor Industries

    - Ruskin

    - Greenheck

  - ACCEPTABLE MANUFACTURERS - SMOKE DAMPERS

    - Nailor Industries

    - Ruskin

    - Greenheck

  - ACCEPTABLE MANUFACTURERS - VOLUME DAMPERS

    - Nailor Industries

    - Ruskin

    - Greenheck

  - ACCEPTABLE MANUFACTURERS - MOTOR ACTUATORS

    - Belimo Air Controls

  - ACCEPTABLE MANUFACTURERS - FLEXIBLE DUCT CONNECT0R

    - Elgen

    - DuroDyne

    - Ventfabrics

  - ACCEPTABLE MANUFACTURERS - ACCESS DOORS

    - Bilco

    - Milcor

    - Nystrom

    - Ventfabrics

  - MATERIALS

    - General:  Non-combustible flexible materials conforming to requirements of ANSI/NFPA 90A for Class 1 air duct materials and UL 181.

    - Fasteners: Rivets, bolts or sheet metal screws.  Fasteners which are visible on the diffuser or grille faces shall be furnished with the terminal device at the factory and match the finish.

      - Sealant:  On-hardening, water base, fire resistive, compatible with mating materials or liquid used with tape or heavy mastic with membrane.  All sealants shall comply with Section 07920 - Joint Sealants and shall meet EQ4.1.

    - Hanger Rod:  Teel, galvanized; threaded both ends, threaded one end or continuously threaded.

  - LOW PRESSURE/LOW VELOCITY DUCT

    - Rigid, rectangular, pre-insulated, closed cell, CFC-free phenoloic foam board conforming to SMACNA Class 6 leakage; factory molded and faced on both sides with 25 micron aluminum foil reinforced with a 5 mm glass tissue mesh; and aluminum flanges.  Duct to contain UL label and other markings required by UL 181 on each full sheet of duct board; UL ratings for closure materials.   Temperature limits to be 250 Degree F inside duct and 150 Degree F ambient temperature surrounding duct; Koolduct to be manufactured by Kingspan.  The use of this material for medium pressure ductwork is PROHIBITED.

    - Thermal Conductivity:  ‘K’ value of 0.13 at 75 Degree F.

    - Moisture Absorption:  Not to exceed 5 percent by weight at 120 Degree F and 95 percent relative humidity for 96 hours when tested in accordance with ASTM C-423.

    - Vapor Barrier Permeability:  0.02 perms maximum when tested in accordance with ASTM E96, Procedure A.

    - Noise Reduction Coefficient:  0.65 minimum when tested in accordance in accordance with ASTM C423, Mounting A.

    - Reinforcements:

          - Tie-Rod Reinforcements:  0.108 inch galvanized-steel wire of length to suit termination method.

          - Reinforcing Rod Washers:  2-1/2 inch square by 0.028 inch thick, galvanized-steel washer with turned edges and volcano-type center hole.

          - Sag-Control Supports:  1/2 inch galvanized steel conduit.

    - Joint Closure Sealing:

      - Minimum 2-1/2 inch wide pressure sensitive tape, glass-fiber-reinforced, aluminum-foil tape complying with UL 181A, Part P and imprinted with required information.

      - Heat Activated Tape:  Minimum 2-1/2 inch wide, glass-fiber-reinforced, foil scrim tape complying with UL 181A, Part H and imprinted with required information.

      - Mastic and Glass Fabric:  Minimum 3 inch wide glass fabric and duct manufacturer’s recommended mastic that complies with UL 181.

      - All sealants shall comply with Section 07920 - Joint Sealants and shall meet EQ4.1.

    - Intake Air Plenum:  Constructed of galvanized steel and containing a drain sump behind the louver for trapping any moisture.  In lieu of a drain sump, sloping the bottom of the plenum 15 degree toward the louver and attaching the bottom of the plenum to the top of the bottom blade of the louver will be approved.

    - Construct tee's, bends and elbows with radius of not less than 1-1/2 times width of duct on centerline.  Where not possible and where rectangular or miter elbows are used, provide single thickness air foil turning vanes.  The use of double wall air foil turning vanes shall be approved if there is no increase in cost.

    - Increase duct sizes gradually, not exceeding 22.5 degree air divergence wherever possible. Ensure air divergence upstream of equipment does not exceed 30 degree. Ensure convergence downstream of equipment does not exceed 45 degree.

    - Construct all branch takeoffs from both the supply and return mains and sub-mains with 45 degree branch takeoff fittings equipped with volume control dampers. Should 45 degree branch takeoffs not be appropriate, two-piece bellmouth or conical takeoffs with volume control dampers will be acceptable.

    - Provide 2 inch high standoff brackets with locking type quadrants for volume control dampers on insulated ducts.  Standoff brackets shall not be required on non-insulated ducts.

    - Connect flexible ducts to phenolic foam ducts with adhesive, draw-band and foil faced duct tape.

    - Seal all transverse joints, longitudinal seams and duct wall penetrations.

    - Provide easements where low pressure ductwork conflicts with piping and structure.  Where easements exceed 10 percent duct area, split into two ducts maintaining original duct area.

    - Use double nuts and lock washers on threaded rod supports.

    - Fabricate rectangular ducts and fittings from duct boards.

    - Fabricate mitered elbows with turning vanes.

    - All branch takeoff connections on supply ducts shall contain volume control dampers in branch ducts.

    - Attach metal components to phenolic foam ducts with galvanized steel washers on opposite surfaces of duct walls.

  - FLEXIBLE AIR DUCT

    - UL 181, Class 1 commercial grade flexible duct rated for 10 inch WG having a minimum R-6 rating and constructed of a vinyl interior liner supported by helically wound spring steel wire with flexible high density glass fiber insulation and enclosed with a metalized spiral reinforced vapor barrier jacket; Model 1200 manufactured by Omniair, Model UPC #016 manufactured by Atco, Series MKE manufactured by Thermaflex or approved equal.  Hard duct drops will not be approved unless waived by the Owner prior to design.

    - Provide flexible duct in one-piece, 2 feet minimum and not to exceed 8 linear feet. Spliced flexible duct is PROHIBITED.

  - TURNING VANE

    - Single thickness, galvanized steel type air foil turning vanes for sizes up to 24 inches in depth and cataloged by a recognized air distribution equipment manufacturer. Provide double thickness air foil turning vanes for sizes greater than 24 inches in depth or in all instances where there is no increase in cost over the single thickness air foil turning vanes.  Provide at all 90 degree square elbows.

  - FIRE DAMPER

    - UL 555, dynamic curtain type, 165 Degree F fusible link fire damper with 22 gauge galvanized steel channel frame, 22 gauge galvanized steel blades, S-slip joint breakaway connection (furnished by Contractor), UL test label with a 1-1/2 hour fire protection rating for penetrations in 1 hour and 2 hour rated partitions and a 3 hour fire protection rating for penetrations in a 3 hour rated partition.  Model D0120 as manufactured by Nailor, Model DIBD2 as manufactured by Ruskin for 1 and 2 hour fire protection rating or approved equal.   Model D0520 as manufactured by Nailor, Model DIBD23 as manufactured by Ruskin for 3 hour fire protection rating or approved equal.

    - Electrical installation shall be performed by the fire alarm specialist and shall comply with Division 16.

  - SMOKE DAMPER

    - UL 555S, Class II leakage smoke damper with 16 gauge galvanized steel hat channel frame with mitered corners reinforced and strengthened with die formed corner gussets, 14 gauge galvanized steel double skin opposed blades, concealed linkage, 1/2 inch plated steel hex axles double thru-bolted at each end of blade to provide positive locking connection, stainless steel sleeve bearings, factory mounted UL approved electric actuator, S-slip joint breakaway connection (furnished by Contractor), UL test label with a 1-1/2 hour fire protection rating for penetrations in 1 hour and 2 hour rated partitions, and a 3 hour fire protection rating for penetrations in a 3 hour rated partition.  Model 1210 as manufactured by Nailor, Model SD36 as manufactured by Ruskin or approved equal.

    - Electrical installation shall be performed by the fire alarm specialist and shall comply with Division 16.

  - OUTSIDE AIR MAKEUP MOTORIZED CONTROL DAMPER

    - Low leakage extruded 6063T5 aluminum hat channel frames with mitered corners and die formed internal braces for rigidity and structural strength; 6 inch depth airfoil type extruded aluminum opposed blades with integral full length structural, reinforcing tubes; blade edge and jam seals of extruded vinyl double edge design; locking quadrant and molded synthetic bearings; 1/2 inch stainless steel hex axles secured tight to airfoil blade; 6 inch x 1/2 inch diameter galvanized steel control shaft with outboard support bearings and actuator linkage concealed in frame.  Dampers capable of moving freely through a full 90 degree arc.  Model CD-50 as manufactured by Ruskin or approved equal.

    - Opposed blade type dampers are to be provided when duct dimensions are greater than 12 inches in depth.  Parallel blade type dampers may be provided when duct dimensions are no greater than 48 inches wide x 12 inches depth.

    - Maximum leakage rates shall not exceed the values when tested at 1 inch WG pressure differential in accordance with AMCA Publication 500.

    - Motor actuator shall be 24 Volt spring return to close, heavy duty, direct coupled electric actuator motor with minimum 75 Inch Lb. of torque, visual position indicator, mounted outside of duct.  Actuator to be as manufactured by Belimo. Refer to Specification Section 15900 - HVAC Instrumentation and Controls.

  - DUCT SMOKE DETECTORS

- A.        Refer to Section 13845 - Fire Alarm System.

  - MANUAL VOLUME CONTROL DAMPER

    - 16 gauge galvanized steel channel frames, 5 inch wide x 16 gauge galvanized steel blades with molded synthetic bearings, 1/2 inch stainless steel hex axles double thru-bolted at each end of blade, 2 inch high standoff brackets on locking type quadrants for insulated duct.  Dampers capable of moving freely through a full 90 degree arc.  Model 1820 as manufactured by Nailor, Model MD-35 as manufactured by Ruskin or approved equal.

    - Opposed blade type dampers are to be provided when duct dimensions are greater than 12 inches in depth.  Parallel blade type dampers may be provided when duct dimensions are no greater than 48 inches wide x 12 inches depth.

  - ACCESS DOOR (DUCT MOUNTED)

    - Minimum 18 inch x 18 inch or maximum size permitted by duct, square gasketed panels of 18 gauge galvanized steel at all locations requiring access to control devices and upstream of coil, electric duct heaters, smoke detectors, motor operated dampers and filters and at a distance of 25 feet from the AHU discharge on both the supply and return air ductwork.

    - Access doors shall be hinged with cam latches and fully gaseketed to the perimeter.

  - FLEXIBLE DUCT CONNECTOR

    - 22 ounce neoprene coated fiberglass fabric connectors with a minimum tear and tensile strength of 110 Lbs. and 250 Lbs, respectfully. Provide in 6 inch minimum to 10 inch maximum lengths at all duct connections to rotating or vibrating equipment such as air handler units, unit ventilators, etc.  Model "Silent Duct" manufactured by Elgen Manufacturing Corporation.

  - DUCT HANGER STRAPS

    - 1 inch x 18 gauge galvanized steel fastened with screws to rectangular ducts and with a bolt to round ducts.

    - Stainless steel suspension cable with ratchet as manufactured by Gripple or approved equal.

  - HANGERS AND SUPPORTS

    - Concrete inserts or structural steel fasteners appropriate for construction materials to which hangers are being attached to.

    - Use concrete anchor fasteners for standard weight aggregate concretes or floor slabs more than 4 inches thick.

  - LOUVERS (EXTERIOR WALL)

    - Refer to Section 10200 - Louvers and Vents.

- EXECUTION

  - INSTALLATION

    - Install ducts under provisions of the manufacturer’s instructions and with a minimum number of joints.

    - Install ducts vertically, horizontally, parallel and perpendicular to the building lines.

    - The duct smoke detector sampling tubes shall extend all the way across the duct and out the opposite side of the duct.  The ends shall be capped and the annular space filled with a listed duct sealant.

    - The duct smoke detector housing shall be marked with the AHU number that it serves along with the device number and whether it is for the supply or return air duct.

    - Provide duct access doors for inspection of the duct smoke detectors.

    - Provide openings in ductwork where required to accommodate thermometers and controllers.  Provide pilot tube openings where required for testing of systems, complete with metal can with spring device or screw to ensure against air leakage.  Where openings are provided in insulated ductwork, install insulation material inside a metal ring.

    - Set plenum doors 6 inches to 12 inches above floor or side of duct.  Arrange door swing so that fan static pressure holds door in a closed position.

    - Locate ducts with sufficient space around the air handler unit to allow normal operating and maintenance activities.

    - The supply and return air ducts shall be provided with 45 degree shoetap takeoffs      and volume dampers.  Should the 45 degree shoetap takeoffs not be appropriate such as for rectangular ducts, two-piece round bellmouth spinin takeoffs such as manufactured by Buckley or two-piece conical takeoffs provided with volume dampers will be acceptable.  THE USE OF ANY 90 DEGREE BRANCH SPININ TAKEOFF SHALL NOT BE APPROVED.

    - Supply and return air duct branches or sub-branches are to be provided with volume dampers for balancing purposes.  Registers are subject to tweaking by unauthorized individuals which will result in unbalancing of the air side system.  THE USE OF ANY AIR TURNING DAMPER OR EXTRACTOR SHALL NOT BE APPROVED.

    - Connect supply air diffusers and return air grilles to low pressure ducts with 8 feet maximum length of flexible air duct.  Should the duct length from the duct takeoff to the supply air diffuser or return air grille exceed 8 feet in length, the difference in length shall be provided with the use of rigid duct of an equivalent cross sectional area.

    - Install flexible air duct on the low pressure ductwork without sharp bends. Minimum centerline radius to be not less than the duct diameter as recommended by SMACNA. Replace crushed or deformed flexible air ducts.  Secure ducts with drawbands, foil faced silver tape and mastic at takeoffs, supply air diffusers and return air grilles.

    - During construction, provide temporary closures on all open ductwork by sealing with a disposable polyethylene sheet to prevent construction dust from entering ductwork system.

    - Attach hangers to concrete floor slabs by the use of drilled concrete anchored fasteners after the concrete slab has cured.  The use of powder actuated fasteners is PROHIBITED.

    - Attach hangers to joists and reinforcing channels that occur within required hanger spacing.  Attach hangers to transmit load to sides and bottom channels and no more than 6 inches from sides of ducts.

    - Install ducts with a clearance of 1 inch and as close to the walls, overhead construction, columns and other structural and permanent enclosure elements of the building.

    - Support horizontal ducts with trapeze-type hangers.

    - Support equipment and duct components and accessories independent of ducts.

    - Locate ducts with sufficient space around the air handler unit to allow normal operating and maintenance activities.

    - Do not install ductwork inside buildings until the building is weather-tight. Replace weather damaged ductwork at no cost to the Owner without any time extension to the Contractor.

    - Provide all necessary structural steel hangers, sheet metal flanges and reinforcements required to install the electric duct heater and other equipment in the duct system.

    - Do not support ductwork from joist cross and lateral bracing or from galvanized steel decking.  Should the deck be constructed of concrete, support from the concrete deck will be permitted.

    - On CAV designed systems, provide a motor-operated, low leakage outside air makeup damper and a manual control volume damper on the outside air makeup ducts connected to the mechanical room air handling unit.  See the mechanical plans for the approximate location of the dampers and fan.  Electrical connection to be performed by electrician.  Refer to Division 16.

    - Install fire or smoke dampers in accordance with code.  Dampers to be dynamic type (static dampers are not approved) and self-supporting designed to provide a positive barrier to air passage when in a closed position.  Dampers to be provided by the sheetmetal contractor and shall be of the S-slip joint breakaway type connection.  Secure all dampers with retaining angles fastened to the sleeve in the wall or floor penetration.  Electrical connections to be performed by fire alarm specialist.  Refer to Division 16.

    - When applicable, the wall opening for a duct penetration through a fire rated wall where a fire damper is not required shall be provided with a 12 inch long by 0.06 inch thick steel sleeve secured to both sides of the wall with steel retaining angles and the annular space between the steel sleeve and the wall opening shall be filled with mineral wool.  See FBC - Mechanical, Chapter 6, Section 607.5.3 for other five exceptions to the use of fire dampers.  Electrical connection shall be performed by the fire alarm specialist.

    - Wall or floor penetrations for fire, smoke or combination fire/smoke dampers shall not be more than 1/8 inch per foot larger on each side of the sleeve penetrating the opening.

    - Where ductwork penetrates a rated wall, seal airtight the annular space between the duct and the wall by filling it with stuffing insulation.  Also seal airtight the perimeter of the smoke damper with a UL approved sealant such as Dow-Corning 999, Dow-Corning Silastic 732 RTV or GE RTV 108.

    - After completion of the fire, smoke and/or the combination fire smoke damper installation, remove the screws provided on the S-slip joint duct breakaway connection used during installation.

  - ADJUSTING AND CLEANING

    - Protect AHU equipment which may be harmed by excessive dirt with temporary 2 inch depth, MERV 13 or 4 inch depth, MERV 13 disposable filters during cleaning.  Refer to Section 15860 - Air Cleaning Devices.

    - Provide adequate access into ductwork for cleaning purposes.

END OF SECTION