# SECTION 15860 (23 40 00)

## AIR CLEANING DEVICES

GENERAL

SECTION INCLUDES

Disposable, extended surface area pleated panel filter.

Filter gauge.

RELATED  SECTIONS

Section 15720 - Air Handling Unit.

Section 15721 - Outside Air Pretreatment Unit.

Section 15722 - Energy Recovery Unit.

Section 15724 - DX Air Handling Unit with Hot Gas Reheat.

Section 15731 - Packaged Suspended DX Air Conditioning Unit.

Section 15732 - Packaged Rooftop DX Air Conditioning Unit.

Section 15733 - Package Grade Mounted DX Air Conditioning Unit.

Section 15810 - Ducts.

Section 15816 - Non-Metal Ducts.

REFERENCES

ANSI/UL 900 - Flammability Test Performance of Air Filter Units

ASHRAE Standard 52.2 - Method of Testing General Ventilation for Removal by Particle Size.

QUALITY ASSURANCE

Filter media shall be ANSI/UL 900 listed, Class 2.

Provide all filters as product of one manufacturer.

Assemble filter components to form filter banks from products of one manufacturer.

SUBMITTALS

Submit product data under provisions of Section 01330 - Submittal Procedures. Submit data on filter media, filter performance, filter assembly and filter frame.

OPERATION AND MAINTENANCE DATA

Submit operation and maintenance data under provisions of Section 01830 - Operation and Maintenance.

Include instructions for operation and changout intervals or monitoring.

DELIVERY, STORAGE AND HANDLING

Deliver product to site under provisions of Section 01663 - Product Delivery, Storage and Handling.

Store and protect product under provisions of Section 01663 - Product Delivery, Storage and Handling.

Store in clean, dry place and protect from weather and construction traffic. Handle carefully to avoid damage to components, enclosures and finish.

PRODUCTS

ACCEPTABLE  MANUFACTURERS

Flanders Filter

Farr

Air Guard

Glasfloss

Waco

DISPOSABLE, EXTENDED AREA PANEL FILTERS (Air Handling Unit)

Media:

UL 900 Class 2, minipleated, water laid micro-fine, fiberglass paper media fabric.

Supported by adhesive-bead pleat separators and bonded to all inside surfaces of frame to eliminate bypass.

Enclosed in moisture resistant carrier board frame.

Nominal size x 4 inch depth.

Rating:

ASHRAE Standard 52.2.

MERV Rating:  MERV 13 with 80-85 percent atmospheric dust spot (ADS) efficiency.

Face Velocity: 500 FPM.

Initial Resistance: 0.50 Inch WG.

Recommended Final Resistance: 0.70 inch to 1.00 inch WG.

DISPOSABLE, EXTENDED AREA PANEL FILTERS (DX Air Conditioning Unit)

Media:

UL 900 Class 2, pleated, lofted, non-woven synthetic or fiberglass media.

Supported and bonded to oxidizing resistant metal grid.

Enclosed in moisture resistant carrier board frame.

Nominal size x 4 inch depth.

Rating:

ASHRAE Standard 52.2.

MERV Rating:  MERV 13 with 80-85 percent atmospheric dust spot (ADS) efficiency.

Face Velocity: 500 FPM.

Initial Resistance: 0.50 Inch WG.

Recommended Final Resistance:  0.60 inch to 0.90 inch WG.

DISPOSABLE, EXTENDED AREA PANEL FILTERS (Packaged Wall Mounted Air Conditioning DX Unit)

Media:

UL 900 Class 2, pleated, lofted, non-woven synthetic or fiberglass media.

Supported and bonded to oxidizing resistant metal grid.

Enclosed in moisture resistant carrier board frame.

Nominal size x 2 inch depth.

Rating:

ASHRAE Standard 52.2.

MERV Rating:  MERV 9 with 40-45 percent atmospheric dust spot (ADS) efficiency.

Face Velocity: 500 FPM.

Initial Resistance: 0.50 Inch WG.

Recommended Final Resistance:  0.60 inch to 0.90 inch WG.

EXECUTION

INSTALLATION

Install air cleaning devices under provisions of the manufacturer's instructions.

During construction, fit all rooftop packaged DX units and air handling units with 4 inch depth, MERV 13 filters.

During construction, provide temporary closures on all open ductwork by sealing with a disposable polyethylene sheet to prevent construction dust from entering ductwork system.

Prevent passage of unfiltered bypass air around filters with felt, rubber or neoprene gaskets.

Prior to test and balance, remove the duct air opening polyethylene sheeting and the temporary set of construction filters and replace with a final set of 4 inch depth, MERV 13 filters on both the DX units and the air handling units.

Provide a differential pressure gauge, such as the Dwyer Magnehelic Series 2000AF, along with a pressure switch as manufactured by Andover, across the AHU filter banks and electrically connect it to a red light on the Central H.O.A. Control Panel which will light to indicate a dirty filter condition.

Do not operate AHUs unless design filters are in place.  If the AHUs are in place and operating prior to building commissioning, 2 inch depth. MERV 8 filters shall be installed on each return air grille in accordance with the latest edition of ASHRAE 52.2.  The MERV 8 filters shall be removed immediately prior to building occupancy.

END OF SECTION