# SECTION 15860 (23 40 00)

## AIR CLEANING DEVICES

- GENERAL

  - SECTION INCLUDES

    - Disposable, extended surface area pleated panel filter.

    - Filter gauge.

  - RELATED  SECTIONS

    - Section 15720 - Air Handling Unit.

    - Section 15721 - Outside Air Pretreatment Unit.

    - Section 15722 - Energy Recovery Unit.

    - Section 15724 - DX Air Handling Unit with Hot Gas Reheat.

    - Section 15731 - Packaged Suspended DX Air Conditioning Unit.

    - Section 15732 - Packaged Rooftop DX Air Conditioning Unit.

    - Section 15733 - Package Grade Mounted DX Air Conditioning Unit.

    - Section 15810 - Ducts.

    - Section 15816 - Non-Metal Ducts.

  - REFERENCES

    - ANSI/UL 900 - Flammability Test Performance of Air Filter Units

    - ASHRAE Standard 52.2 - Method of Testing General Ventilation for Removal by Particle Size.

  - QUALITY ASSURANCE

    - Filter media shall be ANSI/UL 900 listed, Class 2.

    - Provide all filters as product of one manufacturer.

    - Assemble filter components to form filter banks from products of one manufacturer.

  - SUBMITTALS

    - Submit product data under provisions of Section 01330 - Submittal Procedures. Submit data on filter media, filter performance, filter assembly and filter frame.

  - OPERATION AND MAINTENANCE DATA

    - Submit operation and maintenance data under provisions of Section 01830 - Operation and Maintenance.

    - Include instructions for operation and changout intervals or monitoring.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver product to site under provisions of Section 01663 - Product Delivery, Storage and Handling.

    - Store and protect product under provisions of Section 01663 - Product Delivery, Storage and Handling.

    - Store in clean, dry place and protect from weather and construction traffic. Handle carefully to avoid damage to components, enclosures and finish.

    - PRODUCTS

  - ACCEPTABLE  MANUFACTURERS

    - Flanders Filter

    - Farr

    - Air Guard

    - Glasfloss

    - Waco

  - DISPOSABLE, EXTENDED AREA PANEL FILTERS (Air Handling Unit)

    - Media:

      - UL 900 Class 2, minipleated, water laid micro-fine, fiberglass paper media fabric.

      - Supported by adhesive-bead pleat separators and bonded to all inside surfaces of frame to eliminate bypass.

      - Enclosed in moisture resistant carrier board frame.

      - Nominal size x 4 inch depth.

    - Rating:

      - ASHRAE Standard 52.2.

      - MERV Rating:  MERV 13 with 80-85 percent atmospheric dust spot (ADS) efficiency.

      - Face Velocity: 500 FPM.

      - Initial Resistance: 0.50 Inch WG.

      - Recommended Final Resistance: 0.70 inch to 1.00 inch WG.

  - DISPOSABLE, EXTENDED AREA PANEL FILTERS (DX Air Conditioning Unit)

    - Media:

      - UL 900 Class 2, pleated, lofted, non-woven synthetic or fiberglass media.

      - Supported and bonded to oxidizing resistant metal grid.

      - Enclosed in moisture resistant carrier board frame.

      - Nominal size x 4 inch depth.

    - Rating:

      - ASHRAE Standard 52.2.

      - MERV Rating:  MERV 13 with 80-85 percent atmospheric dust spot (ADS) efficiency.

      - Face Velocity: 500 FPM.

      - Initial Resistance: 0.50 Inch WG.

      - Recommended Final Resistance:  0.60 inch to 0.90 inch WG.

  - DISPOSABLE, EXTENDED AREA PANEL FILTERS (Packaged Wall Mounted Air Conditioning DX Unit)

    - Media:

      - UL 900 Class 2, pleated, lofted, non-woven synthetic or fiberglass media.

      - Supported and bonded to oxidizing resistant metal grid.

      - Enclosed in moisture resistant carrier board frame.

      - Nominal size x 2 inch depth.

    - Rating:

      - ASHRAE Standard 52.2.

      - MERV Rating:  MERV 9 with 40-45 percent atmospheric dust spot (ADS) efficiency.

      - Face Velocity: 500 FPM.

      - Initial Resistance: 0.50 Inch WG.

      - Recommended Final Resistance:  0.60 inch to 0.90 inch WG.

      - EXECUTION

  - INSTALLATION

    - Install air cleaning devices under provisions of the manufacturer's instructions.

    - During construction, fit all rooftop packaged DX units and air handling units with 4 inch depth, MERV 13 filters.

    - During construction, provide temporary closures on all open ductwork by sealing with a disposable polyethylene sheet to prevent construction dust from entering ductwork system.

    - Prevent passage of unfiltered bypass air around filters with felt, rubber or neoprene gaskets.

    - Prior to test and balance, remove the duct air opening polyethylene sheeting and the temporary set of construction filters and replace with a final set of 4 inch depth, MERV 13 filters on both the DX units and the air handling units.

    - Provide a differential pressure gauge, such as the Dwyer Magnehelic Series 2000AF, along with a pressure switch as manufactured by Andover, across the AHU filter banks and electrically connect it to a red light on the Central H.O.A. Control Panel which will light to indicate a dirty filter condition.

    - Do not operate AHUs unless design filters are in place.  If the AHUs are in place and operating prior to building commissioning, 2 inch depth. MERV 8 filters shall be installed on each return air grille in accordance with the latest edition of ASHRAE 52.2.  The MERV 8 filters shall be removed immediately prior to building occupancy.

END OF SECTION