# SECTION 16114 (26 05 36)

## CABLE TRAYS

- GENERAL

  - SECTION INCLUDES

    - Provide all labor, materials, necessary equipment and services to complete the Conduits, Fittings and Supports work, as indicated on the drawings, as specified herein or both, except as for item specifically indicated as “NIC ITEMS”.

  - RELATED WORK

    - Section 16120 – Wire and Cables.

    - Section 16132 – Conduit, Fittings and Supports.

  - SUBMITTALS

    - Submit shop drawings and product data under provisions of Section 01330, “Submittal Procedures”.

- PRODUCTS

  - MATERIALS AND COMPONENTS

    - Metallic Cable Tray:  Conform to NEMA VE 1.

    - Ladder – Type Cable Tray:

      - Description:  NEMA VE 1, Class 12A, ladder type center hung tray designated to support 50 pounds per linear foot or as required for cable weight.

      - Material:  Aluminum.

      - Inside Width:  As indicated on drawings (18” wide minimum)

      - Inside Depth:  Four inches (4”).

      - Straight Section Rung Spacing:  Six inches (6”) on center.

      - Inside Radius of Fitting:  Twelve inches (12”).

      - Supports:  The tray system shall be center hung and shall be supported on 4 foot centers by a single 3/8 inch threaded rod or as required for cable weight.

      - Provide all horizontal and vertical 90 degree elbows, tees, and crosses required by the layout shown on the drawings.

      - All edges of cable trays, fittings, and connectors shall be rounded and smooth to prevent injury to the cable during its installation.

      - Provide manufacturer’s standard clamps, hangers, brackets, splice plates, reducer plates, blind ends, barrier strips, connectors, and grounding straps as required.

  - QUALIFICATIONS

    - Manufacturer:  Company specializing in manufacturing products specified in this Section with a minimum of three (3) years experience.

  - WARNING SIGNS

    - Engraved Nameplates:  ½ inch high black letters on yellow laminated plastic nameplate, engraved with the following wording:

      - WARNING:  DO NOT USE CABLE TRAY AS WALKWAY, LADDER, OR SUPPORT.  USE ONLY AS MECHANICAL SUPPORT FOR CABLES AND TUBING!

- EXECUTION

  - INSTALLATION

    - Install in accordance with manufacturer’s instructions and NEMA VE 1.

    - Use expansion connectors where required.

    - Ground and bond cable tray per NFPA 70 Article 392.

      - Provide continuity between tray components.

      - Use anti-oxidant compound to prepare aluminum contact surfaces before assembly.

      - Connections to tray may be made using mechanical or exothermic connectors.

    - Install warning signs at 30 feet centers along cable tray, located to be visible.

    - Support trays in accordance with Section 16132.  Provide supports at each connection point, at the end of each run, and at other points to maintain spacing between support of 4 feet maximum.

    - Provide firestopping using UL listed assemblies for all penetrations of rated walls.  Use metallic sleeves with grounding type bushing on each end.

    - Coordinate cable tray routing with ducts, piping, and work of other trades.

    - The cable tray shall be for the sole use of the Telecommunications and Energy Management (EM and Security) Department.  Any HVAC equipment control wiring if not installed in the cable tray shall be installed in a separate conduit.

END OF SECTION