# SECTION 16134 (26 27 17)

## AUXILIARY TERMINAL PANELS

- GENERAL

  - SECTION INCLUDES

    - Provide all labor, materials, equipment and services to complete the Auxiliary Terminal Panels work, as indicated on the drawings, as specified herein or both, except as for items specifically indicated as “NIC ITEMS.”

  - RELATED WORK

    - Conform under provisions of Division 16 – All applicable sections.

  - SUBMITTALS

    - Submit shop drawings and product data under provisions of Section 01330, “Submittal Procedures.”

    - Submit schedule for each terminal cabinet indicating the system name, function and service of each wire attached to the terminal blocks.

- PRODUCTS

  - GENERAL REQUIREMENT

    - Provide cabinets, with terminal blocks for the splicing of cable for the various wiring systems as shown on the contract drawings.  Cabinets: UL listed and match standard panel boards in appearance and dimension.

  - MATERIALS

    - Cabinets:

      - Fabricated from unpainted, galvanized, code gauge steel, having multiple knockouts, with lapped and riveted or welded corner construction.

      - Of sufficient size to provide a minimum space of four inches between terminal blocks and four inches of gutter space at sides, top and bottom.

      - The size of each terminal cabinet: based upon the number of cables being terminated or spliced within the cabinet, but no smaller than 18 inches high, 18 inches wide and 6 inches deep.

    - Trims:

      - Fabricated from code gauge galvanized sheet steel.

      - Fastened to cabinets by means of machine screws with captive nuts or clamps and self-supporting on the cabinet trim, after trim holding screws have been removed.

      - Trim for flush cabinets: overlap their respective box by at least 3/4 inch all around.

      - Surface trims: the same width and height as the respective box.

      - Doors and trims: each is in one piece, so designed that doors will close without a rabbet.

    - Doors:

      - Fabricated from the same material as the cabinet trim and fastened thereto by continuous concealed hinges.

      - Sized so that terminal blocks do not extend into the side, top or bottom gutter space.

      - Complete with flush type combination lock a catch with key.

      - Doors over 48 inches high: Provide with vault handles, built-in locks and three point catch-fastening door at top, bottom and center.

      - Terminal cabinets wider than 24 inches: provide with multiple doors as required.

      - All terminal cabinets: keyed alike and identical to panel board keying.

    - Backbox interiors, inside trim, door and exterior: painted with a rust inhibiting phosphatized coating after pickling.  Finish of door and exterior: finished in ANSI-61 gray enamel.

    - Terminal cabinets: provide with 3/4-inch thick marine plywood backboard finished with 2 coats of flame retardant flat gray paint.

    - Terminal blocks: factory assembled, channel mounted, rated for 50 volts, with a separate continuous numbering system for each wiring function and be Square D Class 9080, or equivalent I.T.E. or Westinghouse.

- EXECUTION

  - INSTALLATION

    - Provide a typewritten directory with metal frame and clear plastic face upon the interior of the door of each terminal cabinet, indicating the system name, function and service of each wire attached to the terminal blocks.

    - Splice all wiring entering a terminal cabinet as a lug on the terminal block before exiting to serve equipment.  All wiring in terminal cabinets: neatly racked and bundled with non-flammable nylon ties.

    - Terminate conduit in cabinet with lock nut and insulated grounding bushings for feeders or lock nut and insulated bushings for control and/or signal.

    - Terminate wiring on terminal blocks.  Wiring: grouped in accordance with its respective function.

END OF SECTION