# SECTION 16410 (26 28 16)

## CIRCUIT BREAKERS

GENERAL

WORK INCLUDED

Provide all labor, materials, necessary equipment and services to complete the circuit breaker work, as indicated on the drawings, as specified herein or both, except as for items specifically indicated as "NIC ITEMS."

RELATED WORK

Section 16220 - Motor Starters.

Section 16230 – Motor Control Centers.

Section 16400 - Service and Distribution.

Section 16413 - Safety Switches.

Section 16430 – Low Voltage Switchgear

Section 16440 – Switchboards and Panel boards.

SUBMITTALS

Submit product data under provisions of Section 01330, “Submittal Procedures”.

SUBSTITUTIONS

Submit under provisions of 01630, “Product Substitution Procedures”.

Substitutions may be considered when a product becomes unavailable through no fault of the contractor.

REFERENCES

NEMA AB 1 1993 – (National Electrical Manufacturers Association) Molded Case Circuit Breakers and Molded Case Switches

UL 489 – (Underwriters Laboratories Inc.) Molded Case Circuit Breaker Enclosures

UL943 – Standard for Ground Fault Circuit Interrupters

CSA C22.2 No. 5.1 – M91 – (Canadian Standard Association) Molded Case Circuit Breakers

Federal Specification W- C – 375b/GEN – Circuit Breakers, Molded Case; Branch Circuit and Services

National Fire Protection Association NFPA – 70 (National Electric Code)

PRODUCTS

Manufacturers

Square D Company, General Electric, Siemens/ITE, Cutler-Hammer.

Circuit breakers:

Conform to Federal Specification W-C-375a and NEMA Standard AB-1, unless indicated otherwise.

Of the ampere rating, voltage rating, number of poles and class of interrupting capacity (I.C.) as indicated, Interrupting ratings are in root mean square (RMS), symmetrical amperes based on NEMA test procedures.

Lugs and terminals: UL approved for copper-aluminum.

Accessories: 120 volt.

Each circuit breaker: provide a trip unit for each pole with elements providing inverse time delay under overload conditions and instantaneous magnetic trip for short circuit protection, unless indicated as non-automatic.  Trip elements: operate a common trip bar to open all elements.

All circuit breakers shall be bolted-in type, consisting of the number of poles and ampere ratings as noted on the drawings.

Two and three pole breakers shall be of the common trip type.

Molded Case Circuit Breakers

Molded Case Circuit Breakers Characteristics – General

Cicuit Breakers shall be constructed using glass reinforced insulating material.  Current carrying components shall be completely isolated from the handle and the accessory mounting area.

Circuit breakers shall have an over center, trip free, toggle operating mechanism which will provide quick – make, quick – break contact action.  The circuit breaker shall have common tripping of all poles.

The circuit breaker handle shall reside in a tripped position between on and off to provide local trip indication.  Circuit breaker escutcheon shall be clearly marked on and off in addition to providing International I/O markings.

The maximum ampere and UL, IEC, or other certification standards with applicable voltage systems and corresponding interrupting ratings shall be clearly marked on face of circuit breaker.

Circuit breakers shall be factory sealed with a hologram quality mark and shall have date code on face of circuit breaker.

Circuit breaker/ circuit breaker combinations for series connected interrupting ratings shall be listed by UL as a recognized component combinations.  Any series rated combination used shall be marked on the end use equipment along with the statement “Caution – Series Rated System________A Available.  Identical Replacement Component Required.”

Circuit breakers shall be equipped with UL Listed electrical accessories as noted on the associated electrical drawings.  Circuit breaker handle accessories shall provide provisions for locking handle in the On and Off position.

All circuit breakers shall be UL Listed for reverse connection without restrictive line and load markings and be suitable for mounting in any position.

Thermal – Magnetic Circuit Breakers

Circuit breakers shall have a permanent trip unit containing individual thermal and magnetic trip elements in each pole.

Thermal trip elements shall be factory preset and scaled.  Circuit breakers shall be true rms sensing and thermally responsive to protect circuit conductor(s) in a 40 degree ambient temperature.

Circuit breaker frame sizes above 100 amperes shall have a single magnetic trip adjustment located on the front of the circuit breaker (except type Q2, Q2H, and Q2 – H).

Provide UL Listed HACR circuit breakers where required.

Electronic Trip Circuit Breakers With Standard Function Trip System 2000amp maximum

Circuit breaker trip system shall be a micro compressor – based true rms sensing design with sensing accuracy through the thirteenth (13th) harmonic.  Sensor ampere ratings shall be as indicated on the associated electrical drawings.

The integral trip system shall be independent of any external power source and shall contain no less than industrial grade electronic components.

The ampere rating of the circuit breaker shall be determined by the combination of an interchangeable rating plug, the sensor size and the long time pickup adjustment on the circuit breaker.  The sensor size, rating plug and the adjustment positions shall be clearly marked on the face of the circuit breaker.  Circuit breakers shall be Ul Listed to carry 80% or 100% (if service entrance main breaker) of their ampere rating continuously as specified or designed on the associated electrical drawings.

The following time/ current response adjustments shall be provided.  Each adjustment shall have discrete settings and shall be independent of all other adjustments.

Long Time Pickup Instantaneous Pickup

Long Time Delay (Ground Fault Pickup)

Short Time Pickup (Ground Fault Delay (I2t OUT only))

Short Time Delay

Ground Fault Pickup {Service Entrance Main if required or designed.}

Ground Fault Pickup {Service Entrance Main if required or designed.}

A means to seal the trip unit adjustments in accordance with NEC Section 240-6(b) shall be provided.

Local visual trip indication for overload, short circuit and ground fault trip occurrences shall be provided.

Long Time Pickup indication to signal when loading approaches or exceeds the adjusted ampere rating of the circuit breaker shall be provided.

Circuit breaker trip system shall be equipped with an externally accessible test port for use with a Universal Test Set.  Disassembly of the circuit breaker shall not be required for testing.  Test set shall be capable of verifying the operation of all trip functions with or without tripping the circuit breaker.

Insulated Case Circuit Breaker With Full Function Trip System 25000 amp and Above.

Circuit breaker trip system shall be a microprocessor – based true rms sensing design with sensing accuracy through the thirteenth (13th) harmonic.  Sensor ampere ratings shall be as indicated on the associated [schedules], [drawings].

The integral trip system shall be independent of any external power source and shall contain no less than industrial grade electronic components.

Circuit breakers shall be equipped with back-up thermal and magnetic trip system.

The ampere rating of the circuit breaker shall be determined by the combination of an interchangeable rating plug, the sensor size and the long – time pickup adjustment on the circuit breaker.  The sensor size, rating plug and switch adjustments shall be clearly marked on the face of the circuit breaker.  Circuit breakers shall be UL Listed and carry 100% of their ampere rating continuously.

The following time/current response adjustments shall be provided.  Each adjustment shall have discrete settings and shall be independent from all other adjustments.

Long Time Pickup Instantaneous Pickup

Long Time Delay

Short Time Pickup

Short Time Delay

Ground Fault Pickup

Ground Fault Delay

A means to seal the rating plug and trip unit adjustments in accordance with NEC Section 240 – 6(b) shall be provided.

Local visual trip indication for overload, short circuit and ground fault trip occurrences shall be provided..

Long Time Pickup indication to signal when loading approaches or exceeds the adjusted ampere rating of the circuit breaker shall be provided.

Circuit breaker trip system shall be equipped with an externally accessible test port for use with a Universal Test set.  Disassembly of the circuit breaker shall not be required for testing.  Test set shall be capable of verifying the operation of all trip functions with or without tripping the circuit breaker.

EXECUTION

INSTALLATION

Install all circuit breakers as required where indicated on the drawings and where required by the National Electrical Code.

Circuit breaker pick-up level and time delay settings shall be adjusted to values indicated on the associated electrical drawings, schedules, coordination study, and or as indicated by the Engineer of Record.

END OF SECTION