# SECTION 16510 (26 51 00)

## INTERIOR LUMINAIRES

- GENERAL

  - WORK INCLUDED

    - Provide all labor, materials, necessary equipment and services to complete the Luminaires work, as indicated on the drawings, as specified herein or both, except as for items specifically indicated as "NIC ITEMS."

    - Interior Luminaires and Accessories

    - Exit Signs

    - Ballasts/Light Emitting Diode (LED) Drivers

    - Lamps

  - RELATED SECTIONS

    - Section 16050 – Basic Materials and Methods

    - Section 16060 – Grounding

    - Section 16080 – Electrical Inspection and Testing

    - Section 16120 - Wires and Cables.

    - Section 16130 – Raceways and Boxes

    - Section 16132 - Conduits, Fittings and Supports.

    - Section 16138  Outlet Boxes.

    - Section 16140 - Wiring Devices

  - APPLICABLE DOCUMENTS

- The Latest adopted edition of the following codes or standards shall apply to the design and fabrication of the products and equipment to be supplied by this Section.

    - Latest edition of Illuminating Engineering Society of North America (IESNA) handbook.

    - ANSI   C78.379—Electric Lamps—Incandescent and High-Intensity Discharge Reflector Lamps—Classification of Beam Patterns

    - ANSI C82.1—Ballasts for Fluorescent Lamps—Specifications

    - ANSI C82.4—Ballasts for High-Intensity Discharge Lamps (Multiple Supply Type).

    - ANSI C82.16—American National Standard for Light Emitting Diode Drivers—Method of Measurement

    - ANSI/NFPA 70—National Electrical Code

    - ANSI/NFPA 101—Life Safety Code

    - UL 8750—Standard for Light Emitting Diode (LED) Equipment for Use in Lighting Products

    - UL 8750 Standard for Light Emitting Diode (LED) Equipment for Use in Lighting Products

    - UL 1012 – Standard for Light Emitting Diode (LED) drivers

    - State Requirements for Educational Facilities – SREF

  - SUBMITTALS

    - Submit shop drawings and product data under provisions of Section 01330, “Submittal Procedures”.

    - At the Project Consultant's request, submit for review and approval one representative sample of any luminaire or luminaire component required under the contract. Tag the luminaires or components with the name of the project and ship to the address specified by the Project Consultant.  After review, the luminaire or luminaires will be shipped to the Project Consultant at the project for use as a standard.  All charges for these shipments will be prepaid by the Contractor.  Luminaires under the contract: identical with the approved luminaire.  No luminaire used as a sample will be allowed to be installed on the project.  In the event the submissions are disapproved, the luminaires will be returned to the Contractor who will immediately make a new submission of luminaire or luminaires meeting the contract requirements.

    - Provide Photometric data and adjustment factors based on laboratory tests, complying with IESNA Lighting Measurements Testing & Calculation Guides, of each lighting fixture type. The adjustment factors shall be for lamps, ballasts, and accessories identical to those indicated for the lighting fixture as applied in this Project. Solid state LED lighting photometric data based on IES LM-79 laboratory tests of each luminaire type, complete with indicated LED engines, power supplies, operating current in milliamps (mA), and accessories.

    - Provide LED engines, including life based on IES LM-80, output based on IES LM-79 testing methods, CCT, CRI, lumens, operating current in milliamps (mA), and energy-efficiency data.

    - Provide a list of all LED light engine and driver types used on Project; use manufacturers' codes.

    - Provide recommended LED light engine and driver replacement schedule for each lamp type based on manufacturer's listed lamp life ratings

    - The Contractor: submit shop drawings for the Project Consultant's approval of a sufficient size to show necessary detail for each luminaire type, and its components.  Catalog cuts or scale drawings will not be acceptable.

    - Shop drawings include but not be limited to:

      - Manufacturer's dimensioned scale drawings showing in complete detail the fabrication of all luminaires including finished, metal thickness, fabrication methods, support method, ballasts, sockets type of shielding, reflectors, provisions for relamping and all other information to show compliance with the Contract Documents.

      - Submit shop drawings and samples as requested of luminaires for approval before fabrication.  Luminaire details may vary slightly from those shown on drawings provided the changes do not adversely affect size of installation, durability of luminaire, luminaire performance or appearance. Submitted samples may be subjected to photometric testing at an independent testing laboratory, refer to Section 01430, “Quality Assurance”.

  - QUALITY ASSURANCE

    - Conform under provisions of Section 01430, “Quality Assurance”.

    - Materials, equipment and appurtenances as well as workmanship provided under this section shall conform to the highest commercial standard and as specified and as indicated on drawings.  Luminaire parts and components not specifically identified or indicated: made of materials most appropriate for their use or function and as such resistant to corrosion and thermal and mechanical stresses encountered in the normal application and functioning of the luminaires.

    - All cast parts, including die-cast members: of uniform quality, free from blow holes, pores, hard spots, shrinkage defects, cracks or other imperfections that affect strength and appearance, or are indicative of inferior metals or alloys.  Exterior surfaces, which do not otherwise receive a finishing coating: machined, sanded or similarly treated areas, such as extruded metal parts.  All such finished castings: given a minimum of one coat of baked-on clear methacrylate lacquer unless a painted finish is specified.

  - REFERENCES

    - Conform under provisions of Section 01420, “References”.

    - Luminaires and components made under provisions of the N.E.C. and bear the UL label.

  - DELIVERY, STORAGE AND HANDLING

    - Conform under provisions of Section 01663, “Product Delivery, Storage and Handling Requirements”.

    - Luminaries and lighting equipment: delivered, stored and handled to the project complete, including mounting devices, lamps and components necessary for the proper operation of the equipment.

    - It is the Contractor's sole responsibility for proper shop drawing submittal, order and release of orders for any and all luminaries, assurance of delivery dates by manufacturers, etc., in order as to not delay the project in any manner.

  - QUALIFICATIONS

    - Photometric data of independent nationally recognized testing agencies will be accepted.

    - Photometric data of testing laboratories of luminaire manufacturer's may be accepted if certified and approved by the Project Consultant.

  - RECOMMENDED AVERAGE MAINTAINED ILLUMINANCE LEVELS, IN FOOTCANDLES (FC)

- Classroom		60

- Chalkboard Lighting – Provide Exitance Analysis

- Laboratories		60

- Teaching Auditoriums (*)		30-60

- Media Center		60

- Principals & Assistant Principals		60

- Clerical		60

- Physical Education (Gym) (*)		30-50

- Cafeteria		50

- Kitchen		60

- Interior Corridors		30

- Exterior Corridors		10

- Computer Labs (*) (**)		60

- Covered Walkways & Connector Walks	5

- Courtyards		1 (minimum)

- (*)  Provide multiple level switching.

- (**) Indirect systems may be considered when ceilings are at 10’6” minimum, maximum of 250 Footlamberts, with a uniformity ratio of 4:1.

- Provide a minimum of five (5) footcandle lighting in open chiller plants controlled by EMS.

  - WARRANTY

    - Warranty all equipment and the installation to be free of faulty workmanship.

    - Lamps and ballast shall be warranted as a combination installation for a minimum of five (5) years from the date of final Substantial Completion.

    - LED luminaires and drivers shall be warranted for (5) years from the date of Final Substantial Completion.

  - SUBSTITUTIONS

    - Will be considered by the Project Consultant and Owner when submitted per requirements of Division-0, Division-1, and Section 01630-Product Substitution Procedures.

- PRODUCTS

  - FINISHES

    - Luminaire finishes:

      - Applied in a manner that will assure a durable wear-resistant surfacing.

      - Prior to finishing, hot clean surface by accepted chemical means and receive corrosion inhibiting (phosphating) treatment assuring positive paint adhesion.

      - Exposed metal surfaces, except chromium plated parts: given an even coat of high-grade methacrylate lacquer, or transparent epoxy.

      - Aluminum surfaces exposed to weather: receive a duranodic finish for corrosion resistance.

      - Sheet steel luminaire housings, iron and steel parts, which have not received phosphating treatment ("Bonderizing" or similar process) as outlined above or are to be utilized in exterior applications: make corrosion resistant by zinc or cadmium plating, or hot-dip zinc galvanizing after completion of all forming, welding, or drilling operations.

      - Minimum thickness of above protective coatings:

        - Hot galvanized zinc coating - 0.0005 inch.

        - Cadmium plating - 0.0001 inch. Electroplate parts operated under temperatures injurious to hot-dipped galvanizing.

    - Painted reflectors:

      - Completely formed before application of primer and enamel color coat or coats.

      - Reflectors and reflector bodies for fluorescent lamp luminaires, having baked-on white synthetic enamel finish: made of steel of the thickness specified and given a suitable primer and white color coat or coats properly applied.

    - When requested by the Project Consultant, submit a sufficient quantity of flat steel panels having the identical primer and color coat or coats applied in the same manner as proposed for the contract items, for subjection to any one (1) or all of the tests listed herein by an owner approved independent testing laboratory. The panels: suitable size and drilled as necessary for a particular test procedure.  The Contractor: bears the cost of all required tests.

  - LAMPS

    - Provide electric lamps as shown on reviewed shop drawings plus 10 percent additional spare lamps of all types to the Owner at project site upon completion.

    - Lamps as specified for the individual luminaries or lighting equipment: provide in luminaires and lighting equipment leaving these completely lamped and in normal operating condition.

    - All lamps to be TCLP approved whenever available

    - Lamps produced by the following manufacturers are acceptable:

      - General Electric.

      - Osram/Sylvania Lighting.

      - Phillips.

      - Lithonia

      - BCPS approved equal

    - Fluorescent lamps: rapid start, 28-watt, T8 (Octron)(2725 Lumens) 4100K, energy savings unless specifically noted otherwise.

    - Incandescent lamps – Not allowed:

      - Avoid using incandescent light fixtures unless is absolutely necessary.

    - LED lamps:

      - Minimum CRI of 80 with a color temperature of 4100ºK for interior fixtures, and 4000-4500ºK for exterior fixture, unless otherwise noted in the Contract Documents.

      - Minimum rated life of 60,000 hours at 25ºC ambient temperature.

      - LED lighting fixtures shall be assembled in the USA with minimum 80% materials content from the USA.

      - All LED fixtures located within instructional spaces shall have factory installed dimmable control modules built right into the fixture.

      - LED fixtures shall be provided with a minimum 5-year warranty on entire fixture (all components).

      - Luminaires must be rated for -40°C to +50°C operation.

      - Minimum Color Rendering Index (CRI) of 80.

      - Minimum Luminaire efficiency shall be 100 lumens per watt. Small lumen output fixtures (less than 1000 lumens) and decorative fixtures may be below 100 lumens per watt.

      - Fixtures shall be Energy Start or Design Lights Consortium "DLC" labeled / qualified.

  - LED DRIVER REQUIREMENTS

    - Power Supply Units (PSUs) including drivers must meet the following requirements:

      - Must have a minimum efficiency of 85%.

      - Must be rated to operate between -40°C to +50°C

      - Input Voltage: capable of 120 to 277 (±10%) volt, single phase as required by the site.

      - Power supplies can be UL Class I or II output.

      - Operating frequency must be 60 Hz.

      - LED driver and LED module shall be accessible and replaceable from below.

      - Drivers must have a Power Factor (PF) of 0.95 or higher. with integral short circuit, open circuit and overload protection.

      - Drivers must have a Total Harmonic Distortion (THD) of <20%.

      - Drivers must comply with FCC 47 CFR part 15 non-consumer RFI/EMI standards.

      - Drivers must be Reduction of Hazardous Substances (RoHS) compliant.

      - Drivers for fixtures connected to dimmers must be compatible with specified dimming controls.

  - REFLECTORS

    - Reflectors and reflecting cones or baffles: fabricated from #12 aluminum reflector sheets, 0.57: (15 gage) or heavier, all absolutely free of any tooling marks including spinning lines, and free of any marks or indentations caused by riveting or other assembly techniques.  No rivets, springs or other hardware will be visible after installation.

    - Reflectors and baffles: of first quality polished, buffed and anodized finish, "Alzak", and of specular finish color as selected by Project Consultant.  Reflector and baffles: modified elliptical contour and produce no apparent brightness from nadir to 40 degrees above nadir, nor the lamp image nor any part of the lamp be visible from nadir to 40 degrees above nadir.

    - Other aluminum reflectors, where required:

      - Formed and finished as noted on drawings and elsewhere in the specifications.

      - Free from blemishes, scratches, or indentations which would distort their reflective function, and finished by means of the "Alzak" process unless otherwise noted.

    - Submit samples of colored aluminum finished (black, brass, bronze, etc.) for approval before fabrication.

  - LAMP HOLDERS

    - Lamp sockets: Rigidly and securely attached to luminaire enclosure or husk.

      - Incandescent and metallic vapor lamp sockets: Of heavy-duty heat-resistant porcelain type.

      - Plastic or metal sheet sockets: Do not be used unless specified.

      - Fluorescent lamp sockets operating with an open circuit voltage in excess of 300 volts: Of the safety type, and open the supply circuit when the lamp is removed from the sockets.

  - WIRING

    - Wiring between fluorescent lamp holders and associated operating and starting equipment: Of similar or heavier gauge than the leads furnished with the approved types of ballasts and provide equal or better insulating and heat resisting characteristics.  All wiring within luminaire or from the luminaire to the splice with the building wiring: as specified under Section 16120 - Wire and Cables.

    - Wire within housing: entirely covered with flexible woven fiberglass sleeve. Protect wiring with tape or tubing at all points where abrasion may occur. Conceal wiring within luminaire construction except where the luminaire design or mounting dictates otherwise.

    - Connections of wires to terminals of lampholders and other accessories must be made in a neat and workmanlike manner and be electrically and mechanically secure with no protruding loose strands.  The number of wires extending to or from the terminals of a lampholder or other accessory: do not exceed the number, which the accessory is designed to accommodate.

    - Joints in wiring within luminaires and connections of the luminaire wiring to the wiring of the building are as specified under Section 16120 - Wire and Cables.

    - Wiring channels and wire ways: free from projections and rough or sharp edges throughout, and all 	points or edges over which conductors must pass and may be subject to injury or wear shall be rounded or bushed.

    - Insulated bushings: installed at points of entrance and exit of flexible wiring.

    - Junction boxes attached to luminaires: manufactured under provisions of the National Electrical Code and approved for the number of conductors indicated on the drawings.  Supplementary junction boxes installed where required to comply with Code.

    - All wiring connections from the junction boxes to luminaries, either factory made or field made shall be #12 AWG.  Color Coding for the whips is not required.

    - Whips shall not be used for connection from fixture to fixture.

  - FLUORESCENT LAMP BALLASTS

    - Ballasts:

      - Conform to UL and ANSI specifications and display labels and symbols of approval by the UL and of certification by the C.B.M. as tested by the E.T.L.

      - The component parts of the ballast: designed, fabricated, and assembled under provisions of the latest requirements of the N.E.C.

      - Marked "Class P" indicating approved integral ballast protection.

      - Provide fuses in each of the primary leads in addition to the Class P Ballast.

      - Fuse holder: Bussman type 'HLR'.

      - Fuses: Bussman type 'GLR' of proper ampacity.

    - Ballasts: provide safe and reliable operation of the specified lamps. Provide two-lamp ballasts for luminaires with 2 lamps or multiples of 2 lamps.  Three-lamp ballasts are not acceptable.

    - Ballasts installed within each luminaire type shall be identical.  Luminaire design, fabrication, and assembly: such as to prevent overheating or cycling of lamps and ballasts under all conditions.

    - Ballasts: provide the lowest sound rating available for the lamps specified and clearly show their respective sound ratings.  Ballasts found by the Project Consultant to be unduly noisy: replaced without charge prior to acceptance of the job.

    - Ballasts made by the following manufacturers will be accepted:

      - Advance.

      - ULT (Universal Lighting Technology).

      - Osram/Sylvania.

      - Lutron.

    - The School Board of Broward County’s criteria in the selection and application of electronic ballast is as follows:

      - Percent of rated light output at 10 percent under voltage over 80.5 percent.

      - Percent of rated light output at rated voltage over 80.5 percent.

      - Percent of rated light output at 10 percent over voltage over 80 percent.

      - Current Crest Factor less than 1.6.

      - Input power factor over 98 percent.

      - Ballast efficiency factor over 1.15.

      - Total Harmonic distortion less than 12 percent.

    - Provide low temperature ballasts for designated applications such as in low temperature ambient, etc.

    - All ballast shall be multi-volt.

    - All ballast to be used with motion sensors shall be program start.

  - LENSES FOR FLUORESCENT OR LED LUMINAIRES

    - KSH-19 Clear - Luminaire enclosure: KSH-19 clear acrylic manufactured by K-S-H, Inc.

      - Prisms: 3/16-inch square based male cones aligned parallel and perpendicular to the length and width of the panel.

      - Minimum prism height: .080 percent. In a nominal 2 feet x 4 feet luminaire with four 28-watt lamps each rated at 2725 lumens.

      - Maximum average luminance in the 65 degree - 85-degree zone: 360-foot lamberts.

      - The ratio of average to maximum luminance: 2.2 or less at 0 degree Nadir. As manufactured by K.S.H., Inc.

  - MARKING OF LUMINAIRES

    - Mark luminaires designed for voltages other than 110-125 volts circuits.

    - Plainly marked luminaires equipped with ballasts, etc., for operation of rapid start lamps "Use Rapid Start Lamps Only."

    - Plainly marked similarly, luminaires equipped with ballasts, etc., for operation of instant start or other type lamps "Use Instant Start Lamps Only", or as appropriate for other types as required. Markings: clear and located to be readily visible to service personnel but invisible from normal viewing angles when lamps are in place.

  - SOUND TRANSMISSION

    - It is the intent of this Specification that sound transmission through the luminaire units, when spaced as indicated on drawings, shall be sufficiently attenuated to maintain speech privacy between adjoining spaces.

  - LUMINAIRE TRIMS

    - Luminaires shall have finish trim designed for the following types of ceiling systems:

      - Tungstein Lamp when used as a back-up for HID Luminaires H.I.D. Luminaires:

- Ceiling Type                   Trim Type

        - Plaster			IR - Inside Reveal

        - Concrete		IR - Inside Reveal

        - Mineral Tile		OL - Overlap Trim

        - Drywall			OL - Overlap Trim

        - Metal Deck		OL - Overlap Trim

      - Fluorescent or LED Luminaires:

- Ceiling Type	Trim Type

        - Plaster			F - Flanged with Plaster Frame

        - Metal pan		M - Modular - Fit-In

        - Mineral Tile		F - Flanged

        - Drywall			F - Flanged

        - Lay-In			G - Grid

    - Each trim detail:  As shown on the drawings, which are indicative of appearance and dimensional requirements.  The manufacturer trim finish and dimensions: subject to the approval of the Project Consultant.  Flush mounted ceiling trims for rectangular or square recessed luminaires: provide mitered corners continuously welded and smoothed before shop finish is applied.  No lapping of trim metal is permitted.

    - All exposed ceiling trim and inside reveals on all luminaires: painted in a color to match the Engineer sample.

    - Trim of luminaires installed in metal deck:  Match the color of that deck.

  - TYPE X

    - Exit lights:

      - LED lamps shall have 6 inches red letters on white background.

      - Field convertible mounting-end, back or top.

      - Field convertible directional arrows.

      - Each LED exit light shall have a total connected load of less than 2.0 watts.

  - LIGHTING CONTACTOR

    - Electrically operated, mechanically held, double break silver alloy contacts.  Fully rated for tungsten lamp loads, fluorescent lamp loads and general use loads.  Interrupting capacity:  300 percent of rated current. NEMA I enclosure except otherwise specified.

    - As manufactured by:  Asco-920RC, Square 'D' - Class 8903, General Electric - CR160MB, Westinghouse A202.

  - MODULAR RELAY PANEL

    - Comply with UL 508 and UL 916; factory assembled with modular single pole relays, power supplies, and accessory components required for specified performance.

      - Cabinet: Steel with hinged, locking door.

        - Barriers separate low-voltage and line-voltage components

        - Directory: Mounted on back of door.  Identifies each relay as to load groups controlled and each programmed pilot device if any.

        - Control Power Supply: Transformer and full-wave rectifier with filtered dc output.

      - Single-Pole Relays: Mechanically held unless otherwise indicated; split-coil, momentary-pulsed type.

        - Low-Voltage Leads: Plug connector to the connector strip in cabinet and pilot light power where indicated.

        - Rated capacity (Mounted in Relay Panel): 20A, 125V AC for tungsten filaments; 20A, 277V AC for ballasts.

        - Endurance: 50,000 cycles at rated capacity.

        - Mounting: Provision for easy removal and installation in relay cabinet.

  - CLASSROOM LIGHTING CONTROL

    - Provide a motion detector(s) in each teaching space as per SBBC Standards.

    - Sequence of Operations:

      - Overview:  Classroom lighting is controlled by motion sensors in series with normal power wall toggle switches and relay override control of emergency power wall toggle switches for emergency lighting.

        - Normal Operations: When a person enters the classroom, the motion sensor energizes the normal power lighting circuit in the classroom.  If the wall toggle switches are "ON", the normal power lighting fixtures will operate.  If the wall toggle switches are "OFF", the normal power lighting fixtures will not operate until the switch is placed in the "ON" position.  The emergency power lighting fixtures are controlled by a separate wall toggle switch for "ON" or OFF".

        - Emergency Operation: In case of a loss of utility normal power, the emergency generator will operate (starts within 10 seconds) and provide limited power to emergency power light fixtures.  The normal power light fixtures will not operate.  The emergency power light fixtures are override controlled through a relay and will operate "ON", no matter what position its wall toggle switch is in.

        - Slide/Video Show Operation: The wall toggle switches would control the normal power and emergency power light fixtures to allow darkening of the classroom.  In case of a loss of utility normal power, the emergency power light fixtures will operate "ON", no matter what position the wall toggle switch is in.

        - After Hours and Vacant Rooms: The motion sensor will de-energize all lighting circuits, no matter what position the wall toggle switches are in.  The emergency     power lighting fixtures will be energized upon loss of power and generator start.

    - Motion sensors shall be installed following manufacturer’s recommendations.

    - Motion sensors and their power packs must be of the same manufacturer.

    - Motion sensor failure shall leave lights on.

    - Motion sensors shall be provided with a 5 year warranty.

  - TIME SWITCHES (Allowed only when EMS is not available to perform the function)

    - Electronic Time Switches:  Electronic, solid-state programmable units with alphanumeric display; complying with UL 917.

      - Circuitry:  Allow connection of a photoelectric relay as a substitute for on-off function of a program.

      - Astronomic Time Clock capability.

      - Battery Backup:  For schedules and time clock.

    - Electromechanical-Dial time switches:

      - Circuitry:  Allow connection of a photoelectric relay as a substitute for on-off function of a program.

      - Astronomic time dial.

      - Wound-spring reserve carryover mechanism to keep time during power failures, minimum of 16 hours.

  - OUTDOOR PHOTOELECTRIC SWITCHES

    - Description:  Solid state, with dry contacts to operate connected relay, contactor coils, or microprocessor input; complying with UL 773A.

      - Light-Level Monitoring Range:  1.5 to 10 fc, with an adjustment for turn-on and turn-off levels within that range.

      - Time Delay: 15-second minimum, to prevent false operation.

      - Surge Protection:  Metal-oxide varistor, complying with IEEE C62.41.1, IEEE C62.41.2, and IEEE 62.45 for category A1 locations.

      - Mounting:  Twist lock complying with IEEE C136.10, with base-and-stem mounting or stem-and-swivel mounting accessories as required to direct sensor to the north sky exposure.

    - Description: Solid state, with dry contacts to operate connected load, relay, or contactor coils; complying with UL 773.

      - Light-Level Monitoring Range:  1.5 to 10 fc, with an adjustment for turn-on and turn-off levels within that range.

      - Time Delay: 30-second minimum, to prevent false operation.

      - Lightning Arrester: Air-gap type.

      - Mounting:  Twist lock complying with IEEE C136.10, with base.

  - INDOOR PHOTOELECTRIC SWITCHES

    - Ceiling Mounted Photoelectric Switch: Solid-State, light level sensor unit, with separate relay unit, to detect changes in lighting levels that are perceived by the eye.

      - Sensor output: Contacts rated to operate the associated relay, complying with UL 773A.  Sensor shall be powered from the relay unit.

      - Relay unit:  Dry contacts rated for 20A ballast load at 120V and 277V, for 13A tungsten at 120V AC, and for 1hp at 120V AC.  Power supply to sensor shall be 24V DC, 150mA, Class 2 power source as defined in NFPA 70.

      - Light-Level Monitoring Range: 10 to 200 fc, with an adjustment for turn-on and turn-off levels within that range.

      - Time Delay:  Adjustable from 5 to 300 seconds to prevent cycling, with deadband adjustment.

      - Indicator:  Two LEDs to indicate the beginning of on-off cycles.

    - Skylight Photoelectric Sensors:  Solid state, light-level sensor; housed in a threaded, plastic fitting for mounting under skylight, facing up at skylight; with separate relay unit, to detect changes in lighting levels that are perceived by the eye.

      - Sensor output: Contacts rated to operate the associated relay, complying with UL 773A.  Sensor shall be powered from the relay unit.

      - Relay unit:  Dry contacts rated for 20A ballast load at 120V and 277V, for 13A tungsten at 120V AC, and for 1hp at 120V AC.  Power supply to sensor shall be 24V DC, 150mA, Class 2 power source as defined in NFPA 70.

      - Light-Level Monitoring Range: 1000 to 10,000 fc, with an adjustment for turn-on and turn-off levels within that range.

      - Time Delay:  Adjustable from 5 to 300 seconds to prevent cycling, with deadband adjustment.

      - Indicator:  Two LEDs to indicate the beginning of on-off cycles.

  - ILLUMINANCE COMPUTER ANALYSIS

    - Provide illuminance computer analysis for all prototype indoor space and also for all parking lots.

    - For indoor analysis the initial light loss factor shall be taken as the product of the voltage drop factor (0.97) times the ballast factor.

    - Parking lot lighting shall be designed for a maintained minimum of 1 foot candle with a max/min ratio of 12/1.

- EXECUTION

  - INSTALLATION

    - Luminaire locations as indicated on the drawings are generalized and approximate.  Carefully verify future locations with Architectural Plans, reflected ceiling plans and other reference data prior to installation. Check for adequacy of headroom and non-interference with other equipment, such as ducts, pipes or openings.

    - Install ballasts, drivers, lamps, LED’s, and specified accessories at factory.

    - Upon completion of the installation, the luminaires and lighting equipment must be in first class operating order and free from defects in condition and finish.  At time of final inspection, all luminaires and equipment must be fully lamped, and be complete with required lenses of diffusers, reflectors, side panels, louvers or other components necessary for the functioning of the luminaires. Luminaires and equipment: clean and free from dust, plaster or paint spots.  Any reflectors, lenses, 	diffusers, side panels or other parts damaged prior to the final inspection must be replaced by the Contractor.

    - The housings of recessed luminaires: Adequately protected during installation by internal blocking or framing to prevent distortion of sides or dislocation of threaded lugs which, upon completion, must be in perfect alignment and match the corresponding holes in frames or rims.  Holding screws: inserted freely without forcing and remain easily removable for servicing.  Threads intended to receive holding screws: chased after plating and finished to insure easy installation and removal of 	knurled headed screws.

    - Housings: rigidly installed, and adjusted to neat flush fit with the ceiling or other finished mounting surface. No light leaks permitted at the ceiling line or from any visible part or joints of the luminaires.

    - Housings installed directly in concrete: fabricated of hot dip galvanized steel or cast aluminum. Where cast aluminum housings are used, provide two coats of asphaltum paint prior to installation.

    - Provide 1/8-inch thick x 2-inch diameter solid neoprene grommets at every mounting point for all luminaires surface mounted to concrete structure to prevent direct contact of housing to concrete.

    - Adjust all directional luminaires to obtain the most uniform distribution.  Orient all similar luminaires consistently.  Coordinate luminaires with speakers, air grilles, pipes and ductwork.

    - Luminaire bottoms, edges and ends of rows: even.  Rows: straight, aligned and equally spaced in distinct areas.  Clean all luminaires of debris and fingerprints and adjust trim to fit surface snug.

    - Provide all necessary hangers and mounting accessories for a complete installation.

    - Locate the fluorescent luminaires in the equipment rooms to best illuminate the equipment installed. Use chains or rods to support below ducts and pipes as required.  Install after pipes and ducts are in.

    - Test all luminaires, switches and controls for operation.  Replace all lamp burnout’s if their estimated operating period is less than 80 percent rated lamp life prior to final acceptance.

  - SUPPORTS

    - Plaster frames: furnished under this section and installed under another section of the specification. Frames: finished matte white baked enamel unless otherwise noted.

    - Recessed luminaires: Provide complete with mounting devices and accessories, and constructed and mounted as to permit access to wiring.

    - Where necessary to meet Code requirements, construct enclosure housings to provide a one-hour fire rating.

    - Attachment devices: made of formed, rolled or cast metal shapes with the requisite rigidity and strength to maintain continuous alignment of the installed luminaires.

    - Luminaires on suspended ceilings: supported from the floor construction above at each corner by means of a minimum of 4 chains per luminaire or #9 ceiling wire or approved equal.

      - Each chain: capable of supporting 100 pounds.

      - Provide saddle hangers or tie bars attached to runners or between crossbars of ceiling systems as a safety catch.

      - Provide mounting splines or other positive means of maintaining alignment and rigidity.

      - Supporting members: surface passivated, and primed or paint dipped to resist corrosion.

      - Ceiling installation contractor shall coordinate with electrical contractor.

    - Contractor: responsible only for necessary adjustments in ceiling required to install luminaires.

    - Contractor:  Verify all ceiling conditions from the Architectural plans and provide appropriate mounting details for each luminaires.

    - Reflectors:  Attached to housing by means of a length of chain, which will prevent reflector from falling. Ensure that no part of chain is visible after installation when viewed from any angle below 45 from the horizontal.

    - Pendant or surface mounted luminaires: provide with required mounting devices and accessories, including hickeys, stud-extensions, ball-aligners, canopies and stems. Coordinate locations of luminaires in mechanical areas. Mounting stems of pendant luminaires: of the correct length to uniformly maintain the luminaire heights shown on the drawings or established in the field.

  - ADJUSTMENT

    - After the installation of luminaires is completed, adjust luminaires after dark under the supervision of the Project Consultant at no additional cost to the Owner.

    - Upon the completion of the installation of all luminaires, turn on for a continuous period of 48 hours and during that time, replace any burned-out lamps, defective ballasts or fuses, etc.

END OF SECTION