# SECTION 16910 (26 09 00)

## ELECTRIC SYSTEM CONTROLS

- GENERAL

  - SECTION INCLUDES

    - Provide all labor, materials, necessary equipment and services to complete the electrical system control work, as indicated on the drawings, as specified herein or both, except as for items specifically indicated as "NIC ITEMS."

  - RELATED WORK

    - Section 15900 – HVAC Instrumentation and Controls for New Phase Replacement Facilities.

    - Section 15901 – HVAC Instrumentation and Controls for Building Addition to Existing Facilities.

    - Section 15902 – HVAC Instrumentation and Controls for ATC Replacement to Existing Facilities.

    - Section 16220 - Motor Starters.

    - Section 16510 - Interior Luminaires.

    - Section 16520 - Exterior Luminaires.

    - Section 16912 - Mechanical Systems Controls.

  - SUBMITTALS

    - Submit shop drawings and product data under provisions of Section 01330, “Submittal Procedures”.

- PRODUCTS

  - RELAYS

    - Relays: conform to NEMA IC-1 and be heavy type, UL listed, rated at 25 Amps, 120 volts and mounted in NEMA 1 enclosures.

    - Grouped units may be in a common enclosure with a plywood backboard.

    - Relays: as manufactured by Potter & Brumfield of the type as follows:

      - Single Pole Double Throw  (SPDT) - #PR5AY.

      - Double Pole Double Throw  (DPDT) - #PR11AY.

      - Four Pole Double Throw    (4PDT) - #PM17AY.

  - CONTACTORS

    - Contactors: conform to NEMA Standard IC-1. Contactor size and ratings: based on Tables in Part II of IC-1 for enclosed units. Coils: rated 120 volts.

    - Contactor characteristics of size, number of poles, voltage and current: as required or indicated for the load served.

    - Mount units in an individual NEMA 1 enclosure except the units indicated in the panel boards. Contactors electrically operated and mechanically held unless indicated otherwise.

    - Provide a local "open-close" control in, on or by the contactor. Units: as manufactured by Square 'D', General Electric, Westinghouse or Asco. Provide remote control switches with pilot light for each contactor.

- EXECUTION

  - WIRING

    - Use #14 stranded copper wiring for all controls unless noted otherwise.

    - Wiring: comply with N.E.C. Article 725, Class 1, Class 2, Class 3 remote control, signaling and power limited circuits.

    - All wiring: in conduit, except it could be run in the cable tray when available.

END OF SECTION