# SECTION 02533 (33 32 13)

## PACKAGED LIFT STATION

- GENERAL

  - SECTION INCLUDES

    - Low-pressure sewer system consisting of a packaged lift station containing a tank, grinder pump, valves and controls.

  - RELATED SECTIONS

    - Section 02200-Earthwork.

    - Applicable sections of Division 15.

  - REFERENCES

    - ANSI/ASTM D1785:  Polyvinyl Chloride (PVC) Plastic Pipe, Schedules 40, 80 and 120.

    - ANSI/ASTM D2729:  Polyvinyl Chloride (PVC) Sewer Pipe and Fittings.

  - REGULATORY REQUIREMENTS

    - HRS Health Department, Standards for Onsight Sewage Disposal System.

    - Broward County Department of Planning and Environmental Protection, Chapter 27 B. C. C.O., & F. A. C. R 62. 405, 62. 604..

  - SUBMITTALS

    - Submit product data under provisions of general condition, “Submittal Procedures”.

  - DELIVERY, STORAGE AND HANDLING

    - Delivery products to site under provisions of Section 01663, “Product Delivery, Storage and Handling Requirements”, in factory-fabricated protective containers, with factory-installed shipping skids and lifting lugs.

    - Store and protect products under provisions of Section 01663, “Product Delivery, Storage and Handling Requirements”.

    - Store in clean dry place and protect from weather and construction traffic.  Handle carefully to avoid damage to components, enclosures and finish.

- PRODUCTS

  - ACCEPTABLE MANUFACTURERS

    - Gorman-Rupp.

    - Peabody Barnes.

    - Flygt Corporation.

  - LOW PRESSURE SEWER SYSTEM

    - Tank:  Custom molded of fiberglass reinforced polyester (FRP) resin with a nominal wall thickness of 1/4 inch and a net capacity of 120 gallons.  Furnish the tank with 2 leak tight PVC flanges set at 180 Degrees apart for connection to a 4-inch nominal diameter PVC influent sanitary line.

    - Core Unit:  Easily removable cartridge type core assembly containing a grinder pump, motor grinder, controls, check valve, anti-siphon valve and wiring.

    - Pump:  Integral, vertical, rotor, motor driven, solids handling pump containing a mechanical seal.

      - Rotor:  Stainless steel.

      - Stator:  Of a specifically compounded ethylene propylene synthetic elastomer suitable for domestic wastewater service.

      - Pumps: Discharge capacity of 20 GPM at 40 PSIG when operating simultaneously.

    - Grinder:

      - Rotating type with a stationary chrome steel shredding ring with hardened type 400 stainless steel cutter bars.

      - Positioned below the pumping elements.

      - Direct-driven by a single, one-piece motor shaft.

    - Motor:  IL listed, 2 HP, 1725 RPM, 240 Volt, 1 Phase, 60 Hz, capacitor start, ball bearing, squirrel cage inducting type with a low starting current, high starting torque, automatic-reset and integral thermal overload protection.

    - Mechanical Seal:  Provide core with a mechanical seal held in position by a stainless steel spring in order to prevent leakage between the motor and the pump.

    - Check Valve:  Factory installed, gravity operated, flapper-type integral check valve on the discharge pipe.  Valve body: PVC with working parts made of type 300 stainless steel and fabric reinforced synthetic elastomer.

    - Anti-Siphon Valve:  Integral anti-siphoning, air-relief valve on the discharge piping below the check valve.

    - Controls:  Integral in core housing inside a waterproof access cover fastened with stainless steel, tamperproof fasteners and containing level control, overflow indicator light and audible alarm.

  - MISCELLANEOUS MATERIALS

    - Provide all materials, components and accessories not specifically described but required for a complete and proper installation.  Materials: new, first quality and subject to the approval of the Project Consultant.

- EXECUTION

  - INSTALLATION

    - Verify that structures and piping of other trades are complete to the extent that installation of the sewer lift station may commence.

    - Examine all pipes and fittings before connecting to sewer lift station to ensure that no defective materials are incorporated.

    - Inspect complete pumping system for indication of defective workmanship or materials and confirm that necessary corrective measures have been taken.

  - TEST AND ADJUST

    - After installation, test sewer lift station to demonstrate proper operation of unit at performance requirements.

    - Provide engineer of record certification for completion.

END OF SECTION