# SECTION 05120 (05 12 00)

## STRUCTURAL STEEL

- GENERAL

  - SECTION INCLUDES

    - Structural steel framing members, fasteners, connectors, anchors, welding materials, & accessorieis.

  - RELATED SECTIONS

    - Section 01572-Construction Waste Management.

    - Section 03300-Cast-in-Place Concrete.

    - Section 05210-Steel Joists.

    - Section 05310-Steel Deck.

    - Section 05500-Metal Fabrications.

    - Section 07810-Applied Fireproofing:  Fireproof protection to framing and metal deck systems.

  - REFERENCES

    - American Institute of Steel Construction:

      - AISC Code of Standard Practice for Steel Buildings and Bridges.

      - AISC Load and Resistance Factor Design (LFRD) Specification for Structural Steel Buildings.

      - AISC Load and Resistance Factor Design Specification for Single-Angle Members.

      - AISC Specification for Allowable Stress Design of Single-Angle Members.

      - AISC Specification for the Design of Steel Hollow Structural Sections.

      - AISC Specification for Structural Steel Buildings Allowable Stress Design, and Plastic Design.

    - ASTM International:(ASTM)

      - ASTM A36/A36M-Standard Specification for Carbon Structural Steel.

      - ASTM A53/A53M-Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

      - ASTM A108-Standard Specification for Steel Bar, Carbon and Alloy, Cold-Finished.

      - ASTM A123/A123M-Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products.

      - ASTM A153/A153M-Standard Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware.

      - ASTM A307-Standard Specification for Carbon Steel Bolts and Studs, 60 000 PSI Tensile Strength.

      - ASTM A325-Standard Specification for Structural Bolts, Steel, Heat Treated, 120/10P5 ksi Minimum Tensile Strength.

      - ASTM A354-Standard Specification for Quenched and Tempered Alloy Steel Bolts, Studs, and Other Externally Threaded Fasteners.

      - ASTM A449-Standard Specification for Quenched and Tempered Steel Bolts and Studs.

      - ASTM A490-Standard Specification for Structural Bolts, Alloy Steel, Heat Treated, 150 ksi Minimum Tensile Strength.

      - ASTM A500-Standard Specification for Cold-Formed Welded and Seamless Carbon Steel Structural Tubing in Rounds and Shapes.

      - ASTM A529/A529M-Standard Specification for High-Strength Carbon-Manganese Steel of Structural Quality.

      - ASTM A563-Standard Specification for Carbon and Alloy Steel Nuts.

      - ASTM A572/A572M-Standard Specification for High-Strength Low-Alloy Columbium-Vanadium Structural Steel.

      - ASTM A588/A588M-Standard Specification for High-Strength Low-Alloy Structural Steel with 50 ksi (345 MPa) Minimum Yield Point to 4-in. (100-mm) Thick.

      - ASTM A786/A786M-Standard Specification for Hot-Rolled Carbon, Low-Alloy, High-Strength Low-Alloy, and Alloy Steel Floor Plates.

      - ASTM A992/A992M-Standard Specification for Structural Steel Shapes.

      - ASTM E164-Standard Practice for Ultrasonic Contact Examination of Weldments.

      - ASTM E165-Standard Test Method for Liquid Penetrant Examination.

      - ASTM E709-Standard Guide for Magnetic Particle Examination.

      - ASTM F436-Standard Specification for Hardened Steel Washers.

      - ASTM F1554-Standard Specification for Anchor Bolts, Steel, 36, 55, and 105-ksi Yield Strength.

    - American Welding Society:

      - AWS A2.4-Standard Symbols for Welding, Brazing, and Nondestructive Examination.

      - AWS D1.1-Structural Welding Code-Steel.

      - International Organization for Standardization (ISO) 14021–1999; Environmental Labels and Declarations

    - SSPC: The Society for Protective Coatings:

      - SSPC-Steel Structures Painting Manual.

      - SSPC Paint 15-Steel Joist Shop Paint.

      - SSPC Paint 20-Zinc-Rich Primers (Type I - Inorganic and Type II - Organic).

      - SSPC SP 3-Power Tool Cleaning.

      - SSPC SP 6-Commercial Blast Cleaning.

      - SSPC SP 10-Near-White Blast Cleaning.

  - SUBMITTALS

    - Product Data:

      - Recycled Content:

        - Indicate recycled content; indicate percentage of pre-consumer and post-consumer recycled content per unit of product.

        - Indicate relative dollar value of recycled content product to total dollar value of product included in project.

        - If recycled content product is part of an assembly, indicate the percentage of recycled content product in the assembly by weight.

        - If recycled content product is part of an assembly, indicate relative dollar value of recycled content product to total dollar value of assembly.

    - Shop Drawings:

      - Indicate profiles, sizes, spacing, locations of structural members, openings, attachments, and fasteners.

      - Connections.

      - Cambers, loads, and finishes.

      - Indicate welded connections with AWS A2.4 welding symbols. Indicate net weld lengths.

    - Mill Test Reports:  Submit indicating structural strength, destructive and non-destructive test analysis.

    - Manufacturer's Mill Certificate:  Certify products meet or exceed specified requirements.

    - Welders Certificates:  Certify welders employed on the Work, verifying AWS qualification within previous 12 months for weld type used.

  - QUALITY ASSURANCE

***************************************************************************************************************

NOTE TO SPECIFIER:  Select the basis of design used for the Project, and edit the following articles to agree with that basis.

***************************************************************************************************************

    - Perform Work in accordance with the following:

      - AISC Code of Standard Practice for Steel Buildings and Bridges.

      - AISC Specification for Structural Steel Buildings Allowable Stress Design, and Plastic Design.

******[OR]******

      - AISC Load and Resistance Factor Design (LFRD) Specification for Structural Steel Buildings.

      - AISC Specification for the Design of Steel Hollow Structural Sections.

      - AISC Specification for Allowable Stress Design of Single-Angle Members.

******[OR]******

      - AISC Load and Resistance Factor Design Specification for Single-Angle Members.

  - QUALIFICATIONS

    - Fabricator:  Company specializing in performing Work of this section with minimum 5 years documented experience with the following current AISC Certification:

      - Standard Steel Building Structures (STD).

      - Conventional Steel Building Structures (SBD).

    - Erector:  Company specializing in performing Work of this section with minimum 5 years documented experience with the following current AISC Certification:

      - Certified Steel Erector (CSE).

    - Shop Painter:  Company specializing in performing Work of this section with minimum  5 years documented experience.

    - Welders and Welding Procedures:  AWS D.1 qualified within previous 12 months.

- PRODUCTS

  - MATERIALS

    - All manufactured structural steel products are to contain recycled content.

  - STRUCTURAL STEEL

***************************************************************************************************************

NOTE TO SPECIFIER:  Edit the following material selections to agree with Project requirements.

***************************************************************************************************************

    - Structural W-Shapes:  ASTM A992/A992M or ASTM A572/A572M; Grade 50.

    - Structural M-Shapes:  ASTM A36/A36M.,ASTM A529/A529M; Grade 50, or ASTM A572/A572M; Grade 50

    - Structural S-Shapes:  ASTM A36/A36M.,ASTM A529/A529M; Grade 50, ASTM A572/A572M; Grade 50.

    - Structural T-Shapes:  Cut from structural W-shapes.

    - Channels and Angles:  ASTM A36/A36M., ASTM A529/A529M; Grade 50, ASTM A572/A572M; Grade 50.

    - Round Hollow Structural Sections:  ASTM A500, Grade B.

    - Square and Rectangular Hollow Structural Sections:  ASTM A500, Grade B.

    - Structural Pipe:  ASTM A53/A53M, Grade B.

    - Structural Plates:  ASTM A36/A36M.

    - Floor Plates:  ASTM A786/A786M; raised pattern.

    - Sliding Bearing Plates:  Teflon coated.

  - FASTENERS, CONNECTORS, AND ANCHORS

    - Bolts:  ASTM A307; Grade A or B.

      - Finish:  Unfinished or Hot dipped galvanized as noted.

    - High Strength Bolts:  ASTM A325; Type 1or ASTM A490; Type 1.

      - Finish:  Unfinished or Hot dipped galvanized as noted.

    - Nuts:  ASTM A563 heavy hex type.

      - Finish:  Unfinished or Hot dipped galvanized as noted.

    - Washers:  ASTM F436; Type 1, circular, beveled where required.

      - Finish:  Unfinished or Hot dipped galvanized as noted.

    - Shear Connectors:  ASTM A108; Grade B, headed, unfinished and in accordance with AWS D1.1; Type B.

    - Anchor Rods:  ASTM F1554; Grade 55, weldable or ASTM A307; Grade A, as  indicated on Drawings

      - Shape:  Hooked or Straight as indicated on Drawings.

      - Plate Washers:  ASTM A36/A36M.

    - Threaded Rods:  ASTM A36/A36M, ASTM A307; Grade A, ASTM A572/572M; Grade 50, or ASTM A588/A588M; Grade B, as designated on Drawings.

      - Finish: Unfinished, or Hot dipped galvanized as noted.

    - Forged Structural Steel Hardware:

      - Clevises and Turnbuckles: ASTM A108; Grade 1085.

      - Eye Nuts and Eye Bolts: ASTM A108; Grade 1030.

      - Sleeve Nuts:  ASTM A108; Grade 1018.

      - Rod Ends, Yoke Ends and Pins, Cotter Pins, and Coupling Nuts: Carbon steel.

  - WELDING MATERIALS

    - Welding Materials:  AWS D1.1; type required for materials being welded.

  - ACCESSORIES

    - Grout:  Non-shrink type, pre-mixed compound consisting of non-metallic aggregate, cement, water reducing and plasticizing additives, capable of developing minimum compressive strength of 7,000 psi at 28 days.

    - Shop and Touch-Up Primer:  SSPC Paint 15, Type 1, red oxide.

    - Touch-Up Primer for Galvanized Surfaces:  SPC Paint 20 Type I Inorganic.

  - FABRICATION

    - Space shear stud connectors as indicated otherwise on Drawings.

    - Develop required camber for members.

  - FINISH

    - Prepare structural component surfaces in accordance with SPC SP 3, unless otherwise noted to prepare for exposed surfaces or fireproofing

    - Shop prime structural steel members. Do not prime surfaces that will be fireproofed, or in contact with concrete.

    - Galvanizing for Structural Steel Members:  ASTM A123/A123M; minimum 1.2 oz/sq ft coating thickness; galvanize after fabrication.

    - Galvanizing for Fasteners, Connectors, and Anchors:

      - Hot-Dipped Galvanizing: ASTM A153/A153M.

  - SOURCE QUALITY CONTROL AND TESTS

    - Shop test bolted and welded connections as specified for field quality control tests.

- EXECUTION

  - EXAMINATION

    - Section 01300-Administrative Requirements: Verification of existing conditions before starting work.

    - Verify bearing surfaces are at correct elevation.

    - Verify anchors rods are set in correct locations and arrangements with correct exposure for steel attachment.

  - PREPARATION

    - Furnish templates for installation of anchor rods and embedments in concrete and masonry work.

  - ERECTION

    - Allow for erection loads, and for sufficient temporary bracing to maintain structure safe, plumb, and in alignment until completion of erection and installation of permanent bracing.

    - Field weld components and shear connectors indicated on Drawings.

    - Field connect members with threaded fasteners; torque to required resistance, tighten to snug tight for bearing type connections.

    - Do not field cut or alter structural members without approval of Architect/Engineer.

    - After erection, touch up welds and abrasions to match shop finishes.

  - GROUT INSTALLATION

    - Shim bearing plates and equipment supports to proper elevation, snug tighten anchor bolts.

    - Fill void under bearing surface with grout. Install and pack grout to remove air pockets.

    - Moist cure grout.

    - Remove forms after grout is set.  Trim grout edges to form smooth surface, splayed 45 degrees.

    - Tighten anchor bolts after grout has cured for a minimum of 3 days.

  - ERECTION TOLERANCES

    - Maximum Variation From Plumb:  1/4 inch per story, non-cumulative.

    - Maximum Offset From Alignment:  1/4 inch.

  - FIELD QUALITY CONTROL

    - Section 01400-Quality Requirements.

    - Bolted Connections:  Inspect in accordance with AISC specifications.

      - Visually inspect all bolted connections.

    - Welding:

***************************************************************************************************************

NOTE TO SPECIFIER:  Select methods of inspection and locations, and edit the following options for weld inspection, accordingly.

***************************************************************************************************************

      - Certify welders and conduct inspections and tests as required.  Record types and locations of defects found in work. Record work required and performed to correct deficiencies.

      - Visually inspect all welds.

      - Ultrasonic Inspection:  ASTM E164; perform on all full penetration welds.

      - Magnetic Particle Examination:  ASTM E709

      - Liquid Penetrant Examination:  ASTM E165

    - Correct defective bolted connections and welds.

END OF SECTION