# SECTION 05310 (05 31 00)

## STEEL DECK

- GENERAL

  - SECTION INCLUDES

    - Steel floor or roof deck and accessories.

  - RELATED SECTIONS

    - Section 01572-Construction and Waste Management

    - Section 03520-Insulating Concrete.

    - Section 05120-Structural Steel.

    - Section 05210-Steel Joists.

  - REFERENCES

  - International Organization for Standardization (ISO) 14021–1999; Environmental Labels and Declarations

  - SUBMITTALS

    - Product Data:

      - Recycled Content:

        - Indicate recycled content; indicate percentage of pre-consumer and post-consumer recycled content per unit of product.

        - Indicate relative dollar value of recycled content product to total dollar value of product included in project.

        - If recycled content product is part of an assembly, indicate the percentage of recycled content product in the assembly by weight.

        - If recycled content product is part of an assembly, indicate relative dollar value of recycled content product to total dollar value of assembly.

- Include manufacturer’s specifications and installation instructions for each type of decking and accessories.

- 1.	Provide certified test data for mechanical fasteners used instead of welding for fastening deck to supporting structures.

- Shop Drawings:  Show layout and types of deck units, anchorage details, and conditions requiring closure strips, supplementary framing, sump pans, cant strips, cut openings, special jointing, and other accessories.

  - QUALITY ASSURANCE

    - Codes and Standards:  Comply with the following codes and standards:  (Current edition, UON)

      - American Iron and Steel Institute (AISI), Specification for the Design of Cold-Formed Steel Structural Members”.

      - American Welding Society (AWS), D1.3 “Structural Welding Code – Sheet Steel”.

      - Steel Deck Institute (SDI), “Design Manual for Composite Decks, Form Decks, and Roof Decks”.

    - Qualification of Field Welding:  Use qualified welding processes and welding operators according to “Welder Qualification” procedures of AWS.

    - Erector Qualifications:  an experienced erector on comparable size projects (size and type)

- PRODUCTS

  - MANUFACTURERS

    - Subject to compliance with requirements, provide products of one of the following:

      - H. H. Robertson Co.

      - United Steel Deck, Inc.

      - Vulcraft Div., Nucor Corp.

      - Wheeling Corrugating Co.

  - MATERIALS

    - All manufactured steel deck products are to contain recycled content.

    - Steel for Galvanized Metal Deck Units:  ASTM A 446, grade E and A required to comply with SDI Specifications.

    - Miscellaneous Steel Shapes:  ASTM A 36.

    - Shear Connectors:  Headed stud type, ASTM A 108, Grade 1015 or 1020, cold-finished carbon steel, with dimensions complying with AISC specifications.

    - Sheet Metal Accessories:  ASTM A 526, commercial quality galvanized.

    - Galvanizing:  ASTM A 525, G90.

    - Galvanizing Repair:  Where galvanized surfaces are damaged, prepare surfaces and repair according to procedures specified in ASTM A780.

    - Paint:  Manufacturer’s baked-on, rust-inhibitive paint, for application to metal surfaces that have been chemically cleaned and phosphate chemical treated.

    - Flexible Closure Strips:  Manufacturer’s standard vulcanized, closed-cell, synthetic rubber.

  - FABRICATION

    - Form deck units in lengths to span 3 or more supports, with flush, telescoped, or nested 2-inch laps at ends and interlocking or nested side laps, of metal thickness, depth, and width as indicated.

    - Roof Deck Units:  Provide deck configurations complying with SDI “Specifications and Commentary for Steel Roof Deck”.

    - Composite Steel Floor Deck:

      - Fabricate deck units with integral embossing or raised pattern to furnish mechanical bond with concrete slabs.

      - Fabricate open-beam deck units with fluted section having interlocking side laps.

    - Roof Sump Pans:

      - Fabricate from single piece of 0.071 inch minimum (14 gage) galvanized sheet metal with level bottoms and sloping sides to direct water flow to drain.

      - Provide sump pans of adequate size to receive roof drains and with bearing flanges not less than 3 inches wide.

      - Recess pans not less than 1-1/2 inch below roof deck surface unless otherwise shown or required by deck configuration.

      - Holes for drains will be cut in the field by others.

- EXECUTION

  - INSTALLATION

    - Place deck units on supporting steel framework and adjust to final position with ends accurately aligned and bearing on supporting members before being permanently fastened.  Do not stretch or contract side lap interlocks.

    - Align deck units for entire length of run of cells and with close alignment between cells at ends of abutting units. Install deck units and accessories according to manufacturer’s recommendations, Shop Drawings, and as specified.

    - Place deck units flat and square, secured to adjacent framing without warp or deflection.

    - Do not place deck units on concrete supporting structure until concrete has cured and is dry.

    - Coordinate and cooperate with structural steel erector in locating decking bundles to prevent overloading of structural members.

    - Do not use floor deck units for storage or working platforms until permanently secured.

    - Fastening Deck Units:

      - Fasten roof deck units to steel supporting members by not less than 5/8 inch diameter puddle welds or elongated welds of equal strength, spaced not more than 12 inches at every support, and adjust weld size and/or spacing to conform with the requirements of the Contract Documents where indicated.  In addition, secure deck to each supporting member in ribs where side laps occur.

      - Comply with AWS requirements and procedures for manual shielded metal arch welding, appearance and quality of welds, and methods used in correcting welded work.

        - Use welding washers at all metal deck thinner than 22 gage.

      - Pneumatically driven mechanical fasteners may be used instead of welding.  Locate mechanical fasteners and install according to deck manufacturer’s instructions.

      - Mechanically fasten side laps of adjacent deck units between supports, at intervals as shown on the drawings, but not further than 24 inch c/c for floor decks and 12 inch c/c for roof decks.

      - Uplift Loading:  Install and anchor roof deck units to resist gross uplift loading, as noted or shown on the drawings.

    - Cutting and Fitting:  Cut and neatly fit deck units and accessories around other work projecting through or next to the decking, as shown.

    - Reinforcement at Openings:  Provide additional metal reinforcement and closure pieces as required for strength, continuity of decking, and support of other work shown.

    - Roof Sump Pans:  Place over openings provided in roof decking and weld to top decking surface.  Space welds not more than 12 inches o.c. with at least one weld at each corner.

    - Shear Connectors:  Weld shear connectors to supports through decking units according to manufacturer’s instructions.  Do not weld shear connectors through 2 layers (lapped ends) of decking units.  Weld only clean, dry deck surfaces.

    - Closure Strips:  Provide metal closure strips at open uncovered ends and edges of roof decking and in voids between decking and other construction.  Weld into position to provide a complete decking installation.

    - Provide flexible closure strips instead of metal closures, at Contractor’s option, wherever their use will ensure complete closure.  Install with adhesive according to manufacturer’s instructions.

    - Touch-up Painting:  After decking installation, wire brush, clean, and paint scarred areas, welds, and rust spots on top and bottom surfaces of decking units and supporting steel members.

      - Touch-up galvanized surfaces with galvanizing repair paint applied according to manufacturer’s instructions.

      - Touch-up painted surfaces with same type of shop paint used on adjacent surfaces.

      - In areas where shop-painted surfaces are to be exposed, apply touch-up paint to blend into adjacent surfaces.

- END OF SECTION