# SECTION 07190 (07 26 00)

## VAPOR BARRIER

- GENERAL

- SECTION INCLUDES

    - Vapor Barrier is to be installed at all interior slab-on-grade.

  - RELATED SECTIONS

    - Section 02200-Earthwork.

    - Section 03300-Cast-In-Place Concrete.

    - SUBMITTALS

    - Submit properly identified manufacturer’s literature before starting work.

    - QUALITY ASSURANCE

    - Regulatory Requirements (Latest Editions):  Comply with the requirement of Florida Department of Health and Rehabilitative Services (HRS), Office of Radiation Control as stated in “Radon-Resistant Construction Guidelines for Use in Florida”, and Florida Building Code.

- PRODUCTS

- MATERIALS

    - Vapor Barrier:  Ten-mil polyethylene film minimum.

    - Tape:  Type recommended by vapor barrier manufacturer; except at vertical penetrations, use reinforced duct tape.

- EXECUTION

- INSTALLATION

    - Lay vapor barrier over entire area to receive interior slab work.

      - Lay vapor barrier with seams perpendicular to and lapped in direction of concrete pour.

      - Seal all joints by lapping 4 inches minimum and tape all joints.

      - Turn edges up to 4 inches to top of slab.

      - Where expansion joints are indicated at adjacent vertical surfaces, extend vapor barrier beyond expansion joint filler and turn up to top of slab.

      - Do not allow screed supports or other items to penetrate vapor barrier.

    - Extend vapor barrier over surfaces of areas to be protected from vapor or transmission from conditioned space to unconditioned space after placement of insulation.

      - Seal all joints by lapping 4 inches minimum and tape all joints.

      - Repair any punctures or tears before placement of finished surface materials.

    - Continuously tape entire perimeter of vapor barrier to adjacent surfaces; around all pipe penetrations; and vapor membrane joints; to seal and prevent vapor moisture penetration.

    - PROTECTION

    - Protect vapor barrier from damage until permanent covering is in place.

      - Repair punctures and tears in vapor barrier using patches of the material overlapping the puncture or tear a minimum of 12 inches.  Seal with tape.

END OF SECTION