# SECTION 07920 (07 92 00)

## JOINT SEALANTS

- GENERAL

- SECTION INCLUDES

- Sealants and caulking for joints between dissimilar materials and to close other joints.

  - REFERENCES

    - ASTM C 834-Standard Specification for Latex Sealants.

    - ASTM C 919-Standard Practice for Use of Sealants in Acoustical Applications.

    - ASTM C 920-Standard Specification for Elastomeric Joint Sealants.

    - ASTM D 1056-Standard Specification for Flexible Cellular Materials-Sponge or Expanded Rubber.

    - GREENGUARD Product Emission Standard for Children & Schools.

    - Standard Practice for The Testing Of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers, including 2004 Addenda.  California Department of Health Services.

    - SWRI (Sealant, Waterproofing and Restoration Institute):  Sealants: The Professional’s Guide.

    - SUBMITTALS

    - Product Data:  Indicate chemical characteristics, performance criteria, limitations and color chart for all materials.

      - Low Emitting Materials.

        - Submit manufacturer’s Material Safety Data Sheet Indicating VOC limits of all products.

        - Submit manufacturer’s certification that all products comply with Standard Practice for The Testing Of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers, including 2004 Addenda.  California Department of Health Services or GREENGUARD Product Emission Standard for Children & Schools.

        - Samples:  Submit samples of each type of sealant and caulking.

        - Submit manufacturer’s installation instructions.

        - QUALITY ASSURANCE

        - Single source responsibility:  Obtain materials from a single manufacturer.

        - Manufacturer Qualifications:  Company specializing in manufacturing the Products specified in this section with minimum 3 years documented experience.

        - Applicator Qualifications:  Company specializing in performing the work of this section with minimum 5 years documented experience.

        - WARRANTY

        - Replace sealants and caulking which fails because of loss of cohesion or adhesion, or does not cure.

        - Furnish written warranty that work executed under this section is free from defects of material and workmanship for a period of 5 years from date of substantial completion of the entire project.

- PRODUCTS

  - MATERIALS

    - Toxicity/IEQ:  All joint sealant materials are to comply with Standard Practice for The Testing Of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers, including 2004 Addenda.  California Department of Health Services or GREENGUARD Product Emission Standard for Children & Schools.

    - Sealant Type 1:

      - Polyurethane base, one-part, chemical curing.

      - Non-sagging type for application in vertical joints.

      - Capable of being immersed in water, withstand movement up to 25 percent of joint width and satisfactorily applied throughout a temperature range of 40 degrees to 90 degrees Fahrenheit.

      - Shore A hardness:  Minimum 15, maximum 50.

      - Conforming to Requirements of ASTM C920 Type S Grade NS, Class 25, T, NT, O, M, G, I.

      - Non-staining and non-bleeding.

      - SWRI Sealant Validation.

      - Color:  Selected by Project Consultant.

      - Sealant Type 2:

      - Polyurethane base, two-part, chemical curing.

      - Self-leveling type for application in horizontal joints.

      - Capable of being continuously immersed in water, withstand movement of up to 25 percent of joint width and satisfactorily applied throughout a temperature range of 40 degrees to 90 degrees Fahrenheit.

      - Uniform, homogenous, and free from lumps, skins, and coarse particles when mixed.

      - Shore A hardiness:  Minimum 30; maximum 35.

      - Conforming to requirements of ASTM C920 Type M, Grade P, Class 25, Use T, NT, M, G, A, O, I.

      - Non-staining and non-bleeding.

      - Color: Selected by Project Consultant.

      - Sealant Type 3:

      - Polyurethane, two-part, chemical cure.

      - Non-sag type for vertical applications.

      - Capable of being continuously immersed in water; withstand movement up to 50 percent of joint width and satisfactory applied throughout a temperature range of 40 degrees to 90 degrees Fahrenheit.

      - Uniform, homogenous, and free from lumps, skins, and coarse particle when mixed.

      - Shore A hardness:  Minimum 30, Maximum 40

      - Conforming to requirements of ASTM C920 Type M, Grade NS, Class 25 use T, NT, M, G, A, O.

      - Non-Staining and non-bleeding.

      - Color:  Selected by Project Consultant.

      - Sealant Type 4

      - Acrylic base, one-part, solvent curing.

      - Capable of being continuously immersed in water, withstand movement up to 7-1/2 percent of joint width and satisfactorily applied throughout a temperature range of 40 degrees to 90 degrees Fahrenheit.

      - Shore A hardiness:  Maximum 55.

      - Non-staining and non-bleeding.

      - Conforming to requirements of ASTM C834.

      - Color:  Selected by Project Consultant.

      - Sealant Type 5:

      - Silicone base, one-part, neutral curing.

      - Withstand movement up to 50 percent of joint width and satisfactorily applied throughout a temperature range of 40 degrees to 90 degrees Fahrenheit.

      - Shore A hardiness:  Maximum 30.

      - Conforming to requirements of ASTM C920, Type S, Grade NS, Class 50, US = NT, M, G, A.	Selected by Project Consultant.

      - SWRI Sealant validation.

      - Color:  Selected by Project Consultant.

      - Sealant Type 6:

      - Synthetic Butyl Rubber, one-part moisture cure.

      - Non-sag acoustical sealant.

      - Non-hardening, non-bleeding.

      - Unexposed joints only.

      - Sealant Type 7:

      - Silicone base, one-part moisture cure

      - Shore A hardness:  15

      - Conforming to requirements of ASTM C920 Type S, Grade NS, Class 100/50, Use T, NT, M, G. A and O.

      - SWRI sealant validation.

      - Color:  Selected by Project consultant.

      - Back-up Materials:

      - As recommended by caulking or sealant manufacturer and compatible with each material.

      - Preformed material sized to require 25 percent to 50 percent compression upon insertion in joint.

      - Do not use materials impregnated with oil, bitumen or similar materials.

      - Bond Breakers:  Where joints are not of sufficient depth to receive back-up material install polyethylene bond-breaking tape at back of joint.

      - Primer:

      - As recommended by manufacturers of caulking or sealant used.

      - Type that will seal the surfaces and prevent absorption of the vehicle essential to the retention of elasticity by the caulking or sealant compound.

      - Accessories: Provide solvent, cleaning agents and other necessary materials as recommended by the caulking or sealant manufacturer essential for a complete installation.

- EXECUTION

- PREPARATION

- Verify joint dimensions, physical and environmental conditions are acceptable to receive work of this Section.

- Verify that substrate surfaces and joint openings are ready to receive work.

- Verify that joint backing and release tapes are compatible with sealant.

- Remove loose materials and foreign matter, which might impair adhesion of sealant.

- Clean and prime joint under provisions of manufacturer’s instructions.

- Perform preparation under provisions of manufacturer’s instructions.

    - Protect elements surrounding work of this section from damage or disfiguration.

    - INSTALLATION

    - Perform work under provisions of ASTM C 804 for solvent release and ASTM C 790 for latex base sealants.

    - Install sealant under provisions of manufacturer’s instruction.

    - Measure joint dimensions and size materials to achieve required width/depth ratios.

    - Install joint backing to achieve a neck dimension no greater than 1/3 of the joint width.

    - Install sealant free of air pockets, foreign embedded matter, ridged and sags.

    - Apply sealant within recommended temperature range.  Consult manufacturer when sealant cannot be applied within these temperature ranges.

    - Apply generally with caulking gun of proper nozzle size to fit joints.

    - Apply with sufficient pressure to fill joint from backing to surface.

    - For joints in flat surfaces, neatly tool compound slightly concave with proper tools.

    - Execute finishing of caulking around frames with coving tool.

    - As work progresses, immediately remove compound that may accidentally flow onto adjoining surfaces using manufacturer's recommended solvent and cleaners. Remove excess material from joints immediately.

    - At completion, carefully check all joints for damage and repair-damaged joints.

    - Clean adjoining surfaces.

    - Protect sealants and caulking until cured.

  - SCHEDULES

  - Exterior:

      - Perimeters of exterior openings where frames meet exterior facade of building: Type 1 or 3.

      - Expansion and control joints in exterior surfaces of poured-in-place concrete walls: Type 1 or 3.

      - Expansion and control joints in exterior surfaces of pre-cast tilt-up wall panels: Type 7 (unpaintabe) or Type 3 (paintable polyurethane).

      - Exterior joints in horizontal wearing surfaces: Type 2 in areas subject to foot and vehicular traffic; Type 3 at plazas, malls, patios etc.

      - Skylights and glazing:  Type 5.

      - Interior:

      - Seal interior perimeters of exterior openings: Type 1.

      - Expansion and control joints in interior surfaces of poured-in-place concrete walls: Type 1 or Type 3.

      - Expansion and control joints in interior surfaces of pre-cast tilt-up wall panels:  Type 1 or Type 3.

      - Interior control and expansion joints in floor surfaces: Type 1 or Type 2.

      - Perimeters of interior frames:  Type 1.

      - Perimeters of bath fixtures:  Type 4.

      - Exposed interior control joints in drywall:  Type 4.

      - Control joints in drywall, perimeter, and between metal framing and substrate in sound rated partitions:  Type 6.

END OF SECTION